## 全部异常
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.126 | 0算力 | 0.000000 | 风扇异常（丢失/数量不足触发保护停机） | 高 | 风扇异常；若同一时间段后出现 ERROR_SOC_INIT，多为风扇保护后的连带失败，主因仍为风扇检测 | 若同一时间段后出现 ERROR_SOC_INIT，多为风扇保护后的连带失败，主因仍为风扇检测；风扇异常 | 根据日志确认要求风扇数量与实际检测数量（如 only find 3 < 4）；断电后检查四个风扇插头是否插紧、线序是否与控制板丝印一致，必要时对调插头判断是风扇还是接口；确认风扇转速是否异常或为 0；更换不转或信号异常的风扇；若硬件正常仍误报，检查控制板风扇检测电路；ERROR_SOC_INIT 若紧跟 fan lost，多为保护停机连带而非算力板主因 | 2026-04-13 04:59:51 load chain 0 eeprom data 2026-04-13 04:59:51 load chain 1 eeprom data 2026-04-13 04:59:52 load chain 2 eeprom data 2026-04-13 04:59:52 eeprom load ret:0 2026-04-13 04:59:52 eeprom load levels 2026-04-13 05:00:12 Error, fan lost, only find 3 (< 4) 2026-04-13 05:00:12 ERROR_FAN_LOST: fan lost 2026-04-13 05:00:12 stop_mining: fan lost 2026-04-13 05:00:12 ****power off hashboard**** 2026-04-13 05:00:13 ERROR_SOC_INIT: soc init failed! 2026-04-13 05:00:13 stop_mining: soc init failed! 2026-04-13 05:00:13 ****power off hashboard**** | logs_10_102_0_126_MINER-10-102-0-126.txt
10.102.0.130 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T06:17:04.065592Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:18:16.148483Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:43:45.432785Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:44:52.850526Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T09:55:44.498845Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T09:56:52.185818Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T15:57:52.121564Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T16:55:32.069285Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T22:56:32.113608Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T22:57:52.082180Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:20:31.259200Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:21:53.326962Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_130_MINER-10-102-0-130.txt
10.102.0.131 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T01:56:12.581667Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:21.642579Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:29.906107Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:59:41.457200Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:10:39.687533Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:11:48.726708Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:40:44.691433Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:42:03.932650Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:43:12.984118Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:44:24.501529Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:55:31.523167Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:56:54.910367Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_131_MINER-10-102-0-131.txt
10.102.0.150 | 0算力 | 0.000000 | 算力板间温差过大（温度保护停机） | 高 | 温度异常；日志含 Fan check passed，可优先排查单链散热、风道堵塞与导热接触，而非风扇本体故障；若出现 Wait for hashboard cool / Slept … diff =，属温差保护逻辑；重点处理高温链路与积灰 | 日志含 Fan check passed，可优先排查单链散热、风道堵塞与导热接触，而非风扇本体故障；若出现 Wait for hashboard cool / Slept … diff =，属温差保护逻辑；重点处理高温链路与积灰；温度异常 | 根据 STATS/日志确认温差异常链（chain）与 PCB/芯片温度分布；重点清理该链散热片与风道、检查硅脂与散热器接触；与其它正常链互换槽位，判断是单链散热/板卡问题还是槽位风道问题；Fan check passed 时仍可能风道堵塞或单链过热；等待 hashboard cool 后仍报 temp diff too high 时，勿先当总线故障；排除积灰、接触不良后再考虑降频或报修；勿随意放宽固件温差阈值；持续异常需更换算力板或厂家检测 | 2026-04-13 04:59:51 load chain 0 eeprom data 2026-04-13 04:59:51 load chain 1 eeprom data 2026-04-13 04:59:52 load chain 2 eeprom data 2026-04-13 04:59:52 eeprom load ret:0 2026-04-13 04:59:52 eeprom load levels 2026-04-13 04:59:56 Wait for hashboard cool, please wait, this may take up to 2 minutes... 2026-04-13 05:03:56 ERROR_TEMP_TOO_LOW: temp diff too high! 2026-04-13 05:03:56 stop_mining: temp diff too high! 2026-04-13 05:03:56 ****power off hashboard**** "Status": "Alive", "Status": "Alive", 2026-04-13 04:59:42 Open miner sn file /config/sn error | logs_10_102_0_150_MINER-10-102-0-150.txt
10.102.0.151 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-13T03:58:33.279399Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T03:58:33.288710Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T03:59:44.099788Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T03:59:44.117395Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:01:04.256757Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T05:01:04.266453Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:03:56.570684Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T05:03:56.580088Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:05:12.706754Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T05:05:12.716084Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:06:27.174472Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T05:06:27.188605Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_151_MINER-10-102-0-151.txt
10.102.0.155 | 0算力 | 0.000000 | 多块算力板故障致 SOC 停机（芯片数严重不足/CRC） | 高 | 日志中「power off hashboard」为关断算力板动作，勿与 PSU 模块故障混淆 | 日志中「power off hashboard」为关断算力板动作，勿与 PSU 模块故障混淆 | 日志中若多条 Chain 出现「only find … asic」远低于 110，且伴随 ERROR_SOC_INIT，多为多块板同时异常；分别检查各故障链的排线、供电接口；与正常链交叉换槽位判断是板还是槽位/控制板；确认 PSU 各组输出是否稳定，但勿将「power off hashboard」误判为 PSU 本体损坏；必要时逐板更换或送修；若固件支持可尝试仅启用健康链临时恢复部分算力 | 2026-04-13 04:59:51 load chain 0 eeprom data 2026-04-13 04:59:51 load chain 1 eeprom data 2026-04-13 04:59:52 load chain 2 eeprom data 2026-04-13 04:59:52 eeprom load ret:0 2026-04-13 04:59:52 eeprom load levels 2026-04-13 04:59:56 Wait for hashboard cool, please wait, this may take up to 2 minutes... 2026-04-13 05:04:45 Chain 1 only find 91 asic, will power off hash board 1 2026-04-13 05:04:50 Chain 2 only find 0 asic, will power off hash board 2 2026-04-13 05:04:50 ERROR_SOC_INIT: soc init failed! 2026-04-13 05:04:50 stop_mining: soc init failed! 2026-04-13 05:04:50 ****power off hashboard**** "Status": "Alive", | logs_10_102_0_155_MINER-10-102-0-155.txt
10.102.0.156 | 0算力 | 0.000000 | 单链算力板故障致 SOC 停机（芯片数异常/CRC/通信） | 高 | 日志中「power off hashboard」为关断算力板动作，勿与 PSU 模块故障混淆 | 日志中「power off hashboard」为关断算力板动作，勿与 PSU 模块故障混淆 | 根据日志定位异常 Chain（如 find 0 asic、仅 find 部分数量、reg crc error）；断电后重插该链算力板排线与供电，做与正常链互换槽位测试以区分板卡与接口；若故障随板迁移则更换算力板；若固定在槽位则检查控制板与该槽位连线；若固件支持可尝试暂时禁用故障链仅跑健康链（注意功耗与收益） | 2015-01-01 00:00:23 load chain 0 eeprom data 2015-01-01 00:00:24 load chain 1 eeprom data 2015-01-01 00:00:25 load chain 2 eeprom data 2015-01-01 00:00:25 eeprom load ret:0 2015-01-01 00:00:25 eeprom load levels 2026-04-13 01:33:33 Wait for hashboard cool, please wait, this may take up to 2 minutes... 2026-04-13 01:36:46 Chain 1 only find 0 asic, will power off hash board 1 2026-04-13 01:36:48 ERROR_SOC_INIT: soc init failed! 2026-04-13 01:36:48 stop_mining: soc init failed! 2026-04-13 01:36:48 ****power off hashboard**** "Status": "Alive", "Status": "Alive", | logs_10_102_0_156_MINER-10-102-0-156.txt
10.102.0.157 | 0算力 | 0.000000 | 温度传感器通信失败（误报超温/温差保护停机） | 高 | 温度异常；日志含 Fan check passed，可排除风扇本体故障 | 日志含 Fan check passed，可排除风扇本体故障 | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-13 04:59:50 load chain 0 eeprom data 2026-04-13 04:59:51 load chain 1 eeprom data 2026-04-13 04:59:52 load chain 2 eeprom data 2026-04-13 04:59:52 eeprom load ret:0 2026-04-13 04:59:52 eeprom load levels 2026-04-13 04:59:52 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 2026-04-13 04:59:52 fail to read pic temp for chain 0 2026-04-13 04:59:53 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 2026-04-13 04:59:53 fail to read pic temp for chain 0 2026-04-13 04:59:54 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 2026-04-13 04:59:54 fail to read pic temp for chain 0 2026-04-13 04:59:55 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 | logs_10_102_0_157_MINER-10-102-0-157.txt
10.102.0.159 | 低算力(<50TH/s) | 35.063996 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-07T21:10:08.476864Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T21:15:16.995517Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:18.878485Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:06:02.077325Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:20:36.462137Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:16:12.772087Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:36.726948Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:33:21.335733Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:30.532566Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:36:12.111990Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-12T07:38:31.749507Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-12T08:46:39.169679Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_159_MINER-10-102-0-159.txt
10.102.0.160 | 0算力 | 0.000000 | 温度传感器通信失败（误报超温/温差保护停机） | 高 | 温度异常；日志含 Fan check passed，可排除风扇本体故障 | 日志含 Fan check passed，可排除风扇本体故障 | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2015-01-01 00:00:23 load chain 0 eeprom data 2015-01-01 00:00:24 load chain 1 eeprom data 2015-01-01 00:00:25 load chain 2 eeprom data 2015-01-01 00:00:25 eeprom load ret:0 2015-01-01 00:00:25 eeprom load levels 2015-01-01 00:00:25 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 2015-01-01 00:00:25 fail to read pic temp for chain 0 2015-01-01 00:00:26 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 2015-01-01 00:00:26 fail to read pic temp for chain 0 2015-01-01 00:00:27 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 2015-01-01 00:00:27 fail to read pic temp for chain 0 2015-01-01 00:00:28 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 | logs_10_102_0_160_MINER-10-102-0-160.txt
10.102.0.166 | 低算力(<50TH/s) | 43.215888 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-12T00:27:01.002994Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:33:19.624106Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:36.223233Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:37:16.111376Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T07:39:07.376087Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T07:50:27.991553Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:51:40.070002Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:52:40.959476Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:53:50.025441Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T14:54:49.093063Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T14:56:00.944800Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T21:01:00.048485Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_166_MINER-10-102-0-166.txt
10.102.0.170 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-12T23:24:05.688704Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:25:57.719626Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:36:55.988665Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:38:42.272095Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:39:42.980730Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:40:52.286138Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:07.781950Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:18.123839Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:36:26.141135Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:38.507774Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:48:38.066746Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:49:49.754828Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_170_MINER-10-102-0-170.txt
10.102.0.178 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:10.840571Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:44.996662Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:06.868764Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:39:13.602088Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:50:16.128772Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:51:48.520481Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:56:11.585651Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:51.824707Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:59:46.901379Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:01:40.359701Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:12:38.293741Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:13:57.707262Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_178_MINER-10-102-0-178.txt
10.102.0.182 | 低算力(<50TH/s) | 0.001222 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-10T19:40:04.350406Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T02:37:03.987857Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T02:38:13.036699Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T08:39:10.954245Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T08:40:23.528237Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:16:25.706695Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:37.226853Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:19:39.664244Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-11T10:21:06.231500Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-11T10:32:23.028846Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:33:32.588556Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T11:34:32.142730Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_182_MINER-10-102-0-182.txt
10.102.0.186 | 0算力 | 0.000000 | 算力板 EEPROM 读取失败（多链初始化失败，SOC 无法启动） | 高 | 多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 根据 load chain … eeprom / Data load fail / eeprom load ret:-1 定位失败链；逐链重插数据排线与电源，换槽位交叉测试区分板卡与控制板；EEPROM error: CRC … REGION、Fixture data load failed 多为数据损坏或通信问题；多链同时失败优先查共因（排线、控制板 EEPROM 通路、固件版本）；出现 ERROR_SOC_INIT: basic init failed / stop_mining: basic init failed 时，勿先当总线泛化故障；可尝试重刷官方或兼容固件后再测；若单链异常可换板；多链皆失败且排除连接后重点考虑控制板或批量硬件问题 | 2026-04-13 04:59:51 load chain 0 eeprom data 2026-04-13 04:59:51 load chain 1 eeprom data 2026-04-13 04:59:51 EEPROM error: CRC 1ST REGION 2026-04-13 04:59:51 EEPROM error: CRC 1ST REGION 2026-04-13 04:59:52 load chain 1 eeprom data 2026-04-13 04:59:52 EEPROM error: CRC 1ST REGION 2026-04-13 04:59:52 EEPROM error: CRC 1ST REGION 2026-04-13 04:59:52 load chain 1 eeprom data 2026-04-13 04:59:52 EEPROM error: CRC 1ST REGION 2026-04-13 04:59:52 EEPROM error: CRC 1ST REGION 2026-04-13 04:59:52 Data load fail for chain 1. 2026-04-13 04:59:53 load chain 2 eeprom data | logs_10_102_0_186_MINER-10-102-0-186.txt
10.102.0.195 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T01:44:31.005610Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:22.244241Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:47.456785Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:35:04.609146Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-13T02:46:33.544173Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:49:41.242433Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:31:22.678412Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:32:44.484393Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:34:09.610057Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:35:17.806584Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:37:21.229560Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T19:38:20.783405Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_195_MINER-10-102-0-195.txt
10.102.0.200 | 低算力(<50TH/s) | 46.185520 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-13T07:33:35.869363Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:37.466695Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:39.059477Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:40.656954Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:42.254320Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:43.856565Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:45.449510Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:47.047237Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:48.649230Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:50.246648Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:51.839474Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:53.439487Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_200_MINER-10-102-0-200.txt
10.102.0.202 | 低算力(<50TH/s) | 41.786389 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-06T21:29:27.232212Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T08:26:08.872240Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T21:15:41.828549Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:20.537659Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:22:09.947989Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:16:16.281813Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:43.069362Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:59:00.763612Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:49:42.396598Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(3)] 2026-04-12T07:51:08.061955Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:52:09.881748Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T23:22:48.567949Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_202_MINER-10-102-0-202.txt
10.102.0.212 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2 | 2026-04-12T20:27:23.217162Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:20:32.182562Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:21:55.624320Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:24:14.865328Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T23:26:53.736181Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T23:38:10.277289Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:40:17.871809Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:41:16.164111Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:42:42.302467Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:02.997122Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:12.543601Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:36:16.066475Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] | logs_10_102_0_212_MINER-10-102-0-212.txt
10.102.0.217 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:42.312455Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:50.219725Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:32.091030Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T01:39:45.699079Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T01:51:02.585787Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:52:12.134509Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:40:38.679850Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:50.211059Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:44:43.776120Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T02:47:09.676937Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T02:58:24.611768Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:59:36.310376Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_217_MINER-10-102-0-217.txt
10.102.0.219 | 0算力 | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；总线/通信异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2 | 2026-04-13T04:26:01.367955Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:05.247533Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:09.126948Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:13.007294Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:16.886571Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:20.765464Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:24.645559Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:28.523866Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:32.404742Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:36.284877Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:40.166640Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:44.045764Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) | logs_10_102_0_219_MINER-10-102-0-219.txt
10.102.0.221 | 0算力 | 0.000000 | 温度传感器通信失败（误报超温/温差保护停机） | 高 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-13T08:28:03.984506Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:05.583993Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:07.178940Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:08.778284Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:10.373218Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:11.972524Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:13.571917Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:15.164651Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:16.766308Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:18.363343Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:19.958211Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:21.553191Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_221_MINER-10-102-0-221.txt
10.102.0.222 | 低算力(<50TH/s) | 40.143830 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2018-03-09T12:36:25.718243Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:26.814643Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:26.939383Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:26.984231Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2018-03-09T12:36:27.912710Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:29.507489Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:31.102627Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:32.695286Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:33.340623Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:33.353505Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2018-03-09T12:36:34.290202Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:35.885202Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_222_MINER-10-102-0-222.txt
10.102.0.228 | 0算力 | 0.000000 | 算力板部分失效（多块链 Dead，仅部分链工作） | 高 | 末段 [DEVS]：Dead=2，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 末段 [DEVS]：Dead=2，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 根据末段 [DEVS] 确认 Dead / Alive 链编号；断电后检查 Dead 链对应算力板数据排线与电源接头；将故障链与正常链互换槽位或交叉到同型号矿机，判断故障随板还是随槽位/控制板；仅单链或部分链工作时总算力约为额定三分之一属常见现象；矿池 Alive 不能排除板级失效；若链长期保持 Dead，更换算力板或送修；必要时导出含启动阶段的完整日志查初始化错误 | 2026-04-13T08:39:51.497444Z [INFO] Connection closed by the server 2026-04-13T08:42:40.807750Z [ERROR] connection dropped due to pool inactivity 2026-04-13T08:42:40.807942Z [ERROR] Stratum read failure 2026-04-13T08:42:40.808543Z [INFO] Connection closed by the server 2026-04-13T08:50:04.358322Z [INFO] Connection closed by the server "Status": "Alive", "Status": "Dead", "Status": "Dead", "Status": "Alive", "Status": "Dead", "Status": "Dead", "CurtailMode": "None", | logs_10_102_0_228_MINER-10-102-0-228.txt
10.102.0.229 | 低算力(<50TH/s) | 48.911060 | 算力板部分失效（多块链 Dead，仅部分链工作） | 高 | 末段 [DEVS]：Dead=2，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 末段 [DEVS]：Dead=2，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 根据末段 [DEVS] 确认 Dead / Alive 链编号；断电后检查 Dead 链对应算力板数据排线与电源接头；将故障链与正常链互换槽位或交叉到同型号矿机，判断故障随板还是随槽位/控制板；仅单链或部分链工作时总算力约为额定三分之一属常见现象；矿池 Alive 不能排除板级失效；若链长期保持 Dead，更换算力板或送修；必要时导出含启动阶段的完整日志查初始化错误 | 2018-03-09T12:36:27.446583Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:27.526751Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2018-03-09T12:36:27.936897Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:28.034736Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2018-03-09T12:36:34.052247Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:34.102162Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2018-03-09T12:36:34.536324Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:34.607179Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2018-03-09T12:36:40.556232Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:40.571917Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 3/5 - asic enumeration failure] 2018-03-09T12:36:41.040345Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:41.077198Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 3/5 - asic enumeration failure] | logs_10_102_0_229_MINER-10-102-0-229.txt
10.102.0.237 | 低算力(<50TH/s) | 0.001334 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,3 | 2026-04-13T00:00:45.675467Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:50.696548Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:20.111247Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:36.444750Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-02T22:54:16.214241Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(2)] 2026-04-02T23:07:52.134770Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-02T23:25:00.239831Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-03T14:00:10.074971Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-04T06:10:46.398872Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-04T16:59:27.152655Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-04T17:20:51.686853Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-04T17:44:37.989186Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_237_MINER-10-102-0-237.txt
10.102.0.242 | 0算力 | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-13T04:08:23.523437Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:28.517525Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:33.387979Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:38.281030Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:43.299771Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:47.920146Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:52.650050Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:57.393194Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:09:02.098499Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:09:06.991437Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:09:12.076245Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:09:21.694247Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded | logs_10_102_0_242_MINER-10-102-0-242.txt
10.102.0.244 | 低算力(<50TH/s) | 32.295371 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-13T01:34:49.117430Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-04T19:19:12.720482Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:17.959985Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:23.200011Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:28.440665Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:33.677445Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:38.920569Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:44.160976Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:49.402023Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:54.640269Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:59.880515Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:20:05.120870Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_244_MINER-10-102-0-244.txt
10.102.0.249 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-12T23:22:23.749681Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:23:55.082185Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:26:08.546280Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:37:11.096786Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:38:47.815359Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:39:51.620900Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:41:26.102377Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:31.660973Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:51.593122Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:30.380972Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-13T01:39:21.313187Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-13T01:50:37.316431Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_249_MINER-10-102-0-249.txt
10.102.1.13 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:07.785496Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:18.629562Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:46:59.869853Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(1)] 2026-04-13T01:48:29.144609Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:56:19.588452Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:33.546896Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:40.965208Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:59:58.739460Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:11:05.955576Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:12:16.662583Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:40:38.708059Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:50.215051Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_13_MINER-10-102-1-13.txt
10.102.1.14 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T03:58:25.539557Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:00:15.829560Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:24.877453Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:03:09.656304Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:04:18.724225Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:05:26.990746Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:06:38.539422Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:17:36.702608Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:18:45.756501Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:19:49.730896Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:20:58.779487Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:35.739524Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_14_MINER-10-102-1-14.txt
10.102.1.15 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-13T01:58:50.290062Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:42.696150Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:42:53.294206Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:03.542514Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:03:13.918412Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:04:33.775062Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:00:01.595653Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(3)] 2026-04-10T18:20:05.426114Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T20:35:36.231473Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-10T20:41:58.962154Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-10T21:45:23.203257Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(3)] 2026-04-10T22:17:18.745655Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_15_MINER-10-102-1-15.txt
10.102.1.19 | 低算力(<50TH/s) | 0.173572 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 |  | logs_10_102_1_19_MINER-10-102-1-19.txt
10.102.1.1 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2 | 2026-04-13T03:59:25.630682Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:37:53.107734Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:39:00.513696Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:40:10.062423Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:44:27.320054Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:45:36.886794Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T09:54:39.797327Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T09:55:47.702023Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T15:56:46.984900Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T15:57:54.911618Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T22:47:00.526275Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T22:48:23.717110Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_1_MINER-10-102-1-1.txt
10.102.1.21 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T02:41:58.685998Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:43:06.100010Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:44:19.285996Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:55:22.132594Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:56:29.803797Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:57:38.605734Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:58:50.049911Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:00:24.534006Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:38.517412Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:03:09.729862Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:04:18.788263Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:05:27.033653Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_21_MINER-10-102-1-21.txt
10.102.1.22 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:01.926663Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:15.179519Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:36:57.504855Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-13T01:39:46.794159Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:50:45.371192Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:51:52.792564Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:56:11.658676Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:20.718199Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:28.944419Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:59:40.455214Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:10:38.825574Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:11:47.884367Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_22_MINER-10-102-1-22.txt
10.102.1.29 | 0算力 | 0.000000 | 算力板部分失效（芯片数量严重不足） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时 | 算力板/芯片异常；网络/矿池连接异常 | 定位异常算力板并单板测试；检查该板排线、供电及散热状态；复位或升级固件后复测芯片识别数量；若芯片长期缺失，安排维修或更换算力板；当前日志涉及 HB:1 | 2026-04-11T10:47:31.642939Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(3)] 2026-04-11T10:59:01.790224Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T11:08:18.963545Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-11T11:15:11.126472Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-11T11:22:31.754091Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-11T11:33:48.337826Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T11:43:45.592055Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-11T12:45:04.892686Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T12:46:02.217591Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-11T19:13:44.283842Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T19:14:55.865241Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T01:18:37.901754Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_29_MINER-10-102-1-29.txt
10.102.1.2 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-10T02:35:39.792621Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:51.332943Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:05:23.669483Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:06:32.485487Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:21:36.102303Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:22:55.855540Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T21:47:53.028271Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-11T10:16:26.017922Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:37.577353Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:45:00.397577Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-12T23:20:32.371572Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:22:03.581055Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_2_MINER-10-102-1-2.txt
10.102.1.36 | 0算力 | 0.000000 | 算力板 EEPROM 读取失败（多链初始化失败，SOC 无法启动） | 高 | 矿机服务异常/接口超时；多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 根据 load chain … eeprom / Data load fail / eeprom load ret:-1 定位失败链；逐链重插数据排线与电源，换槽位交叉测试区分板卡与控制板；EEPROM error: CRC … REGION、Fixture data load failed 多为数据损坏或通信问题；多链同时失败优先查共因（排线、控制板 EEPROM 通路、固件版本）；出现 ERROR_SOC_INIT: basic init failed / stop_mining: basic init failed 时，勿先当总线泛化故障；可尝试重刷官方或兼容固件后再测；若单链异常可换板；多链皆失败且排除连接后重点考虑控制板或批量硬件问题 | [ 0.523162@0] clkmsr ffd18004.meson_clk_msr: failed to get msr ring reg0 [ 0.641932@0] dmi: Firmware registration failed. [ 1.514706@3] Initramfs unpacking failed: junk in compressed archive [ 2.007720@1] i2c i2c-1: of_i2c: modalias failure on /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 2.011544@1] i2c i2c-1: Failed to create I2C device for /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 3.143979@2] defendkey: probe of defendkey failed with error -22 [ 3.892256@1] hub 2-0:1.0: config failed, hub doesn't have any ports! (err -19) [ 4.058196@0] thermal thermal_zone0: binding zone soc_thermal with cdev thermal-cpufreq-0 failed:-22 [ 5.682684@3] meson6-dwmac ff3f0000.ethernet eth0: fail to init PTP. 2026-04-13 04:58:57 get test_loop_securely_find_asic_num failed 2026-04-13 04:59:05 fail to write 0:1 2026-04-13 04:59:05 fail to read 0:1 | logs_10_102_1_36_MINER-10-102-1-36.txt
10.102.1.38 | 0算力 | 0.000000 | 部分算力板失效（初始化/ASIC枚举失败） | 高 | 若 SUMMARY 仍有总算力，属低算力而非零算力 | 若 SUMMARY 仍有总算力，属低算力而非零算力 | 断电后检查故障算力板与控制板之间的电源线、数据线是否插紧、有无氧化；将故障板与正常板互换槽位或交叉到另一台同型号矿机，判断是板卡还是接口/控制板问题；在 LuxOS 中对异常板尝试手动复位或重新上电（若界面支持）；若多次 enumeration 后仍被永久关闭，按硬件损坏流程送修或更换算力板 | 2026-04-13T04:59:36.188876Z [ERROR] Initialization of hashboard failed 2026-04-13T04:59:36.196649Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-13T04:59:36.626499Z [ERROR] Initialization of hashboard failed 2026-04-13T04:59:36.707480Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-13T04:59:37.118495Z [ERROR] Initialization of hashboard failed 2026-04-13T04:59:37.213132Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-13T04:59:42.590497Z [ERROR] Initialization of hashboard failed 2026-04-13T04:59:42.672008Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-13T04:59:43.126464Z [ERROR] Initialization of hashboard failed 2026-04-13T04:59:43.179701Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-13T04:59:43.618495Z [ERROR] Initialization of hashboard failed 2026-04-13T04:59:43.686128Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] | logs_10_102_1_38_MINER-10-102-1-38.txt
10.102.1.41 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T02:40:36.539440Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:45.601388Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:42:53.872765Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:44:05.387662Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:55:02.809725Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:56:11.882618Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:57:15.857200Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:58:24.913388Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:00:16.568811Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:25.631242Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:03:09.738494Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:04:18.799280Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_41_MINER-10-102-1-41.txt
10.102.1.44 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-12T01:28:04.431374Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:33:35.375406Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:37:50.000090Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T14:34:57.246640Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T14:36:06.179846Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T20:37:05.120892Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T20:38:26.041203Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:20:22.517252Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:21:42.082836Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:24:04.616680Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:26:15.171824Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:37:14.763139Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_44_MINER-10-102-1-44.txt
10.102.1.46 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；电源异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:25.167850Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:34.730288Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:04:10.193167Z [ERROR] Tuner error: {ERR:H2} Stage 14: Zero MCR on hashboards [Address(1)] 2026-04-13T02:29:00.952660Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(1)] 2026-04-13T02:40:59.290232Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:42:10.965816Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:06:40.934241Z [ERROR] Tuner error: {ERR:H2} Stage 4: Zero MCR on hashboards [Address(1)] 2026-04-13T03:21:40.819562Z [ERROR] Tuner error: {ERR:H2} Stage 4: Zero MCR on hashboards [Address(1)] 2026-04-13T03:33:29.380954Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:34:42.134627Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T04:35:42.167067Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T04:36:50.098018Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_46_MINER-10-102-1-46.txt
10.102.1.58 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T03:57:40.680911Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T03:58:48.440248Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 9 (expected: 0x1366 received: 0x1f7f) 2026-04-13T05:00:36.367246Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:01:47.926055Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 19 of read_register(reg=0x0) doesn't match chip count 110: reply 0x14 missing 2026-04-13T05:03:14.989696Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:04:24.311126Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 9 (expected: 0x1366 received: 0xe06) 2026-04-13T05:05:37.549461Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x0) 2026-04-13T05:06:45.246451Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:17:44.633431Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:18:57.901575Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 9 (expected: 0x1366 received: 0xc10) 2026-04-13T06:19:57.132840Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T06:21:08.652147Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 20 (expected: 0x1366 received: 0x0) | logs_10_102_1_58_MINER-10-102-1-58.txt
10.102.1.60 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:50.018908Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:59.072978Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:17.888864Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:38:37.723303Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:49:35.985169Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:50:43.410387Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:56:13.636698Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:22.694155Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:41.497298Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:00:01.340103Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:10:59.273660Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:12:06.690143Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_60_MINER-10-102-1-60.txt
10.102.1.64 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:36.122588Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:44.843033Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:13.564552Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:38:43.537863Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:49:44.243395Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:50:51.943488Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:56:11.595965Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:20.629748Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:45.929957Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:00:08.642893Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:11:07.712727Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:12:19.186399Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_64_MINER-10-102-1-64.txt
10.102.1.65 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-13T02:11:33.960126Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T02:12:47.937910Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T02:12:47.947028Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T02:40:48.324962Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T02:40:48.334386Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T02:42:04.324996Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T02:42:04.339291Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T02:43:18.691908Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T02:43:18.705246Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T02:44:32.067011Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T02:44:32.076295Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T02:55:39.412617Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_1_65_MINER-10-102-1-65.txt

## 0算力
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.126 | 0算力 | 0.000000 | 风扇异常（丢失/数量不足触发保护停机） | 高 | 风扇异常；若同一时间段后出现 ERROR_SOC_INIT，多为风扇保护后的连带失败，主因仍为风扇检测 | 若同一时间段后出现 ERROR_SOC_INIT，多为风扇保护后的连带失败，主因仍为风扇检测；风扇异常 | 根据日志确认要求风扇数量与实际检测数量（如 only find 3 < 4）；断电后检查四个风扇插头是否插紧、线序是否与控制板丝印一致，必要时对调插头判断是风扇还是接口；确认风扇转速是否异常或为 0；更换不转或信号异常的风扇；若硬件正常仍误报，检查控制板风扇检测电路；ERROR_SOC_INIT 若紧跟 fan lost，多为保护停机连带而非算力板主因 | 2026-04-13 04:59:51 load chain 0 eeprom data 2026-04-13 04:59:51 load chain 1 eeprom data 2026-04-13 04:59:52 load chain 2 eeprom data 2026-04-13 04:59:52 eeprom load ret:0 2026-04-13 04:59:52 eeprom load levels 2026-04-13 05:00:12 Error, fan lost, only find 3 (< 4) 2026-04-13 05:00:12 ERROR_FAN_LOST: fan lost 2026-04-13 05:00:12 stop_mining: fan lost 2026-04-13 05:00:12 ****power off hashboard**** 2026-04-13 05:00:13 ERROR_SOC_INIT: soc init failed! 2026-04-13 05:00:13 stop_mining: soc init failed! 2026-04-13 05:00:13 ****power off hashboard**** | logs_10_102_0_126_MINER-10-102-0-126.txt
10.102.0.130 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T06:17:04.065592Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:18:16.148483Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:43:45.432785Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:44:52.850526Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T09:55:44.498845Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T09:56:52.185818Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T15:57:52.121564Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T16:55:32.069285Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T22:56:32.113608Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T22:57:52.082180Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:20:31.259200Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:21:53.326962Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_130_MINER-10-102-0-130.txt
10.102.0.131 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T01:56:12.581667Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:21.642579Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:29.906107Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:59:41.457200Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:10:39.687533Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:11:48.726708Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:40:44.691433Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:42:03.932650Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:43:12.984118Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:44:24.501529Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:55:31.523167Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:56:54.910367Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_131_MINER-10-102-0-131.txt
10.102.0.150 | 0算力 | 0.000000 | 算力板间温差过大（温度保护停机） | 高 | 温度异常；日志含 Fan check passed，可优先排查单链散热、风道堵塞与导热接触，而非风扇本体故障；若出现 Wait for hashboard cool / Slept … diff =，属温差保护逻辑；重点处理高温链路与积灰 | 日志含 Fan check passed，可优先排查单链散热、风道堵塞与导热接触，而非风扇本体故障；若出现 Wait for hashboard cool / Slept … diff =，属温差保护逻辑；重点处理高温链路与积灰；温度异常 | 根据 STATS/日志确认温差异常链（chain）与 PCB/芯片温度分布；重点清理该链散热片与风道、检查硅脂与散热器接触；与其它正常链互换槽位，判断是单链散热/板卡问题还是槽位风道问题；Fan check passed 时仍可能风道堵塞或单链过热；等待 hashboard cool 后仍报 temp diff too high 时，勿先当总线故障；排除积灰、接触不良后再考虑降频或报修；勿随意放宽固件温差阈值；持续异常需更换算力板或厂家检测 | 2026-04-13 04:59:51 load chain 0 eeprom data 2026-04-13 04:59:51 load chain 1 eeprom data 2026-04-13 04:59:52 load chain 2 eeprom data 2026-04-13 04:59:52 eeprom load ret:0 2026-04-13 04:59:52 eeprom load levels 2026-04-13 04:59:56 Wait for hashboard cool, please wait, this may take up to 2 minutes... 2026-04-13 05:03:56 ERROR_TEMP_TOO_LOW: temp diff too high! 2026-04-13 05:03:56 stop_mining: temp diff too high! 2026-04-13 05:03:56 ****power off hashboard**** "Status": "Alive", "Status": "Alive", 2026-04-13 04:59:42 Open miner sn file /config/sn error | logs_10_102_0_150_MINER-10-102-0-150.txt
10.102.0.151 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-13T03:58:33.279399Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T03:58:33.288710Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T03:59:44.099788Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T03:59:44.117395Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:01:04.256757Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T05:01:04.266453Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:03:56.570684Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T05:03:56.580088Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:05:12.706754Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T05:05:12.716084Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:06:27.174472Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T05:06:27.188605Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_151_MINER-10-102-0-151.txt
10.102.0.155 | 0算力 | 0.000000 | 多块算力板故障致 SOC 停机（芯片数严重不足/CRC） | 高 | 日志中「power off hashboard」为关断算力板动作，勿与 PSU 模块故障混淆 | 日志中「power off hashboard」为关断算力板动作，勿与 PSU 模块故障混淆 | 日志中若多条 Chain 出现「only find … asic」远低于 110，且伴随 ERROR_SOC_INIT，多为多块板同时异常；分别检查各故障链的排线、供电接口；与正常链交叉换槽位判断是板还是槽位/控制板；确认 PSU 各组输出是否稳定，但勿将「power off hashboard」误判为 PSU 本体损坏；必要时逐板更换或送修；若固件支持可尝试仅启用健康链临时恢复部分算力 | 2026-04-13 04:59:51 load chain 0 eeprom data 2026-04-13 04:59:51 load chain 1 eeprom data 2026-04-13 04:59:52 load chain 2 eeprom data 2026-04-13 04:59:52 eeprom load ret:0 2026-04-13 04:59:52 eeprom load levels 2026-04-13 04:59:56 Wait for hashboard cool, please wait, this may take up to 2 minutes... 2026-04-13 05:04:45 Chain 1 only find 91 asic, will power off hash board 1 2026-04-13 05:04:50 Chain 2 only find 0 asic, will power off hash board 2 2026-04-13 05:04:50 ERROR_SOC_INIT: soc init failed! 2026-04-13 05:04:50 stop_mining: soc init failed! 2026-04-13 05:04:50 ****power off hashboard**** "Status": "Alive", | logs_10_102_0_155_MINER-10-102-0-155.txt
10.102.0.156 | 0算力 | 0.000000 | 单链算力板故障致 SOC 停机（芯片数异常/CRC/通信） | 高 | 日志中「power off hashboard」为关断算力板动作，勿与 PSU 模块故障混淆 | 日志中「power off hashboard」为关断算力板动作，勿与 PSU 模块故障混淆 | 根据日志定位异常 Chain（如 find 0 asic、仅 find 部分数量、reg crc error）；断电后重插该链算力板排线与供电，做与正常链互换槽位测试以区分板卡与接口；若故障随板迁移则更换算力板；若固定在槽位则检查控制板与该槽位连线；若固件支持可尝试暂时禁用故障链仅跑健康链（注意功耗与收益） | 2015-01-01 00:00:23 load chain 0 eeprom data 2015-01-01 00:00:24 load chain 1 eeprom data 2015-01-01 00:00:25 load chain 2 eeprom data 2015-01-01 00:00:25 eeprom load ret:0 2015-01-01 00:00:25 eeprom load levels 2026-04-13 01:33:33 Wait for hashboard cool, please wait, this may take up to 2 minutes... 2026-04-13 01:36:46 Chain 1 only find 0 asic, will power off hash board 1 2026-04-13 01:36:48 ERROR_SOC_INIT: soc init failed! 2026-04-13 01:36:48 stop_mining: soc init failed! 2026-04-13 01:36:48 ****power off hashboard**** "Status": "Alive", "Status": "Alive", | logs_10_102_0_156_MINER-10-102-0-156.txt
10.102.0.157 | 0算力 | 0.000000 | 温度传感器通信失败（误报超温/温差保护停机） | 高 | 温度异常；日志含 Fan check passed，可排除风扇本体故障 | 日志含 Fan check passed，可排除风扇本体故障 | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-13 04:59:50 load chain 0 eeprom data 2026-04-13 04:59:51 load chain 1 eeprom data 2026-04-13 04:59:52 load chain 2 eeprom data 2026-04-13 04:59:52 eeprom load ret:0 2026-04-13 04:59:52 eeprom load levels 2026-04-13 04:59:52 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 2026-04-13 04:59:52 fail to read pic temp for chain 0 2026-04-13 04:59:53 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 2026-04-13 04:59:53 fail to read pic temp for chain 0 2026-04-13 04:59:54 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 2026-04-13 04:59:54 fail to read pic temp for chain 0 2026-04-13 04:59:55 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 | logs_10_102_0_157_MINER-10-102-0-157.txt
10.102.0.160 | 0算力 | 0.000000 | 温度传感器通信失败（误报超温/温差保护停机） | 高 | 温度异常；日志含 Fan check passed，可排除风扇本体故障 | 日志含 Fan check passed，可排除风扇本体故障 | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2015-01-01 00:00:23 load chain 0 eeprom data 2015-01-01 00:00:24 load chain 1 eeprom data 2015-01-01 00:00:25 load chain 2 eeprom data 2015-01-01 00:00:25 eeprom load ret:0 2015-01-01 00:00:25 eeprom load levels 2015-01-01 00:00:25 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 2015-01-01 00:00:25 fail to read pic temp for chain 0 2015-01-01 00:00:26 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 2015-01-01 00:00:26 fail to read pic temp for chain 0 2015-01-01 00:00:27 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 2015-01-01 00:00:27 fail to read pic temp for chain 0 2015-01-01 00:00:28 fail to read tsensor by iic, chain: 0, slave: 72, addr: 0 | logs_10_102_0_160_MINER-10-102-0-160.txt
10.102.0.170 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-12T23:24:05.688704Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:25:57.719626Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:36:55.988665Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:38:42.272095Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:39:42.980730Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:40:52.286138Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:07.781950Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:18.123839Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:36:26.141135Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:38.507774Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:48:38.066746Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:49:49.754828Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_170_MINER-10-102-0-170.txt
10.102.0.178 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:10.840571Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:44.996662Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:06.868764Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:39:13.602088Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:50:16.128772Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:51:48.520481Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:56:11.585651Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:51.824707Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:59:46.901379Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:01:40.359701Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:12:38.293741Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:13:57.707262Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_178_MINER-10-102-0-178.txt
10.102.0.186 | 0算力 | 0.000000 | 算力板 EEPROM 读取失败（多链初始化失败，SOC 无法启动） | 高 | 多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 根据 load chain … eeprom / Data load fail / eeprom load ret:-1 定位失败链；逐链重插数据排线与电源，换槽位交叉测试区分板卡与控制板；EEPROM error: CRC … REGION、Fixture data load failed 多为数据损坏或通信问题；多链同时失败优先查共因（排线、控制板 EEPROM 通路、固件版本）；出现 ERROR_SOC_INIT: basic init failed / stop_mining: basic init failed 时，勿先当总线泛化故障；可尝试重刷官方或兼容固件后再测；若单链异常可换板；多链皆失败且排除连接后重点考虑控制板或批量硬件问题 | 2026-04-13 04:59:51 load chain 0 eeprom data 2026-04-13 04:59:51 load chain 1 eeprom data 2026-04-13 04:59:51 EEPROM error: CRC 1ST REGION 2026-04-13 04:59:51 EEPROM error: CRC 1ST REGION 2026-04-13 04:59:52 load chain 1 eeprom data 2026-04-13 04:59:52 EEPROM error: CRC 1ST REGION 2026-04-13 04:59:52 EEPROM error: CRC 1ST REGION 2026-04-13 04:59:52 load chain 1 eeprom data 2026-04-13 04:59:52 EEPROM error: CRC 1ST REGION 2026-04-13 04:59:52 EEPROM error: CRC 1ST REGION 2026-04-13 04:59:52 Data load fail for chain 1. 2026-04-13 04:59:53 load chain 2 eeprom data | logs_10_102_0_186_MINER-10-102-0-186.txt
10.102.0.195 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T01:44:31.005610Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:22.244241Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:47.456785Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:35:04.609146Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-13T02:46:33.544173Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:49:41.242433Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:31:22.678412Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:32:44.484393Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:34:09.610057Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:35:17.806584Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:37:21.229560Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T19:38:20.783405Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_195_MINER-10-102-0-195.txt
10.102.0.212 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2 | 2026-04-12T20:27:23.217162Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:20:32.182562Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:21:55.624320Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:24:14.865328Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T23:26:53.736181Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T23:38:10.277289Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:40:17.871809Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:41:16.164111Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:42:42.302467Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:02.997122Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:12.543601Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:36:16.066475Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] | logs_10_102_0_212_MINER-10-102-0-212.txt
10.102.0.217 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:42.312455Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:50.219725Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:32.091030Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T01:39:45.699079Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T01:51:02.585787Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:52:12.134509Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:40:38.679850Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:50.211059Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:44:43.776120Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T02:47:09.676937Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T02:58:24.611768Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:59:36.310376Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_217_MINER-10-102-0-217.txt
10.102.0.219 | 0算力 | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；总线/通信异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2 | 2026-04-13T04:26:01.367955Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:05.247533Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:09.126948Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:13.007294Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:16.886571Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:20.765464Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:24.645559Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:28.523866Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:32.404742Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:36.284877Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:40.166640Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:26:44.045764Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) | logs_10_102_0_219_MINER-10-102-0-219.txt
10.102.0.221 | 0算力 | 0.000000 | 温度传感器通信失败（误报超温/温差保护停机） | 高 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-13T08:28:03.984506Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:05.583993Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:07.178940Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:08.778284Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:10.373218Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:11.972524Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:13.571917Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:15.164651Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:16.766308Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:18.363343Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:19.958211Z [WARN] Temperature Sensor Read Failed 2026-04-13T08:28:21.553191Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_221_MINER-10-102-0-221.txt
10.102.0.228 | 0算力 | 0.000000 | 算力板部分失效（多块链 Dead，仅部分链工作） | 高 | 末段 [DEVS]：Dead=2，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 末段 [DEVS]：Dead=2，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 根据末段 [DEVS] 确认 Dead / Alive 链编号；断电后检查 Dead 链对应算力板数据排线与电源接头；将故障链与正常链互换槽位或交叉到同型号矿机，判断故障随板还是随槽位/控制板；仅单链或部分链工作时总算力约为额定三分之一属常见现象；矿池 Alive 不能排除板级失效；若链长期保持 Dead，更换算力板或送修；必要时导出含启动阶段的完整日志查初始化错误 | 2026-04-13T08:39:51.497444Z [INFO] Connection closed by the server 2026-04-13T08:42:40.807750Z [ERROR] connection dropped due to pool inactivity 2026-04-13T08:42:40.807942Z [ERROR] Stratum read failure 2026-04-13T08:42:40.808543Z [INFO] Connection closed by the server 2026-04-13T08:50:04.358322Z [INFO] Connection closed by the server "Status": "Alive", "Status": "Dead", "Status": "Dead", "Status": "Alive", "Status": "Dead", "Status": "Dead", "CurtailMode": "None", | logs_10_102_0_228_MINER-10-102-0-228.txt
10.102.0.242 | 0算力 | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-13T04:08:23.523437Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:28.517525Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:33.387979Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:38.281030Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:43.299771Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:47.920146Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:52.650050Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:08:57.393194Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:09:02.098499Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:09:06.991437Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:09:12.076245Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-13T04:09:21.694247Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded | logs_10_102_0_242_MINER-10-102-0-242.txt
10.102.0.249 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-12T23:22:23.749681Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:23:55.082185Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:26:08.546280Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:37:11.096786Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:38:47.815359Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:39:51.620900Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:41:26.102377Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:31.660973Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:51.593122Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:30.380972Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-13T01:39:21.313187Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-13T01:50:37.316431Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_249_MINER-10-102-0-249.txt
10.102.1.13 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:07.785496Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:18.629562Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:46:59.869853Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(1)] 2026-04-13T01:48:29.144609Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:56:19.588452Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:33.546896Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:40.965208Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:59:58.739460Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:11:05.955576Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:12:16.662583Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:40:38.708059Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:50.215051Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_13_MINER-10-102-1-13.txt
10.102.1.14 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T03:58:25.539557Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:00:15.829560Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:24.877453Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:03:09.656304Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:04:18.724225Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:05:26.990746Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:06:38.539422Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:17:36.702608Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:18:45.756501Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:19:49.730896Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:20:58.779487Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:35.739524Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_14_MINER-10-102-1-14.txt
10.102.1.15 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-13T01:58:50.290062Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:42.696150Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:42:53.294206Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:03.542514Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:03:13.918412Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:04:33.775062Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:00:01.595653Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(3)] 2026-04-10T18:20:05.426114Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T20:35:36.231473Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-10T20:41:58.962154Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-10T21:45:23.203257Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(3)] 2026-04-10T22:17:18.745655Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_15_MINER-10-102-1-15.txt
10.102.1.1 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2 | 2026-04-13T03:59:25.630682Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:37:53.107734Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:39:00.513696Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:40:10.062423Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:44:27.320054Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:45:36.886794Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T09:54:39.797327Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T09:55:47.702023Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T15:56:46.984900Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T15:57:54.911618Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T22:47:00.526275Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T22:48:23.717110Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_1_MINER-10-102-1-1.txt
10.102.1.21 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T02:41:58.685998Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:43:06.100010Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:44:19.285996Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:55:22.132594Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:56:29.803797Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:57:38.605734Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:58:50.049911Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:00:24.534006Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:38.517412Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:03:09.729862Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:04:18.788263Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:05:27.033653Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_21_MINER-10-102-1-21.txt
10.102.1.22 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:01.926663Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:15.179519Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:36:57.504855Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-13T01:39:46.794159Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:50:45.371192Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:51:52.792564Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:56:11.658676Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:20.718199Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:28.944419Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:59:40.455214Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:10:38.825574Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:11:47.884367Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_22_MINER-10-102-1-22.txt
10.102.1.29 | 0算力 | 0.000000 | 算力板部分失效（芯片数量严重不足） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时 | 算力板/芯片异常；网络/矿池连接异常 | 定位异常算力板并单板测试；检查该板排线、供电及散热状态；复位或升级固件后复测芯片识别数量；若芯片长期缺失，安排维修或更换算力板；当前日志涉及 HB:1 | 2026-04-11T10:47:31.642939Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(3)] 2026-04-11T10:59:01.790224Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T11:08:18.963545Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-11T11:15:11.126472Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-11T11:22:31.754091Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-11T11:33:48.337826Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T11:43:45.592055Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-11T12:45:04.892686Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T12:46:02.217591Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-11T19:13:44.283842Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T19:14:55.865241Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T01:18:37.901754Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_29_MINER-10-102-1-29.txt
10.102.1.2 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-10T02:35:39.792621Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:51.332943Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:05:23.669483Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:06:32.485487Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:21:36.102303Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:22:55.855540Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T21:47:53.028271Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-11T10:16:26.017922Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:37.577353Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:45:00.397577Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-12T23:20:32.371572Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:22:03.581055Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_2_MINER-10-102-1-2.txt
10.102.1.36 | 0算力 | 0.000000 | 算力板 EEPROM 读取失败（多链初始化失败，SOC 无法启动） | 高 | 矿机服务异常/接口超时；多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 根据 load chain … eeprom / Data load fail / eeprom load ret:-1 定位失败链；逐链重插数据排线与电源，换槽位交叉测试区分板卡与控制板；EEPROM error: CRC … REGION、Fixture data load failed 多为数据损坏或通信问题；多链同时失败优先查共因（排线、控制板 EEPROM 通路、固件版本）；出现 ERROR_SOC_INIT: basic init failed / stop_mining: basic init failed 时，勿先当总线泛化故障；可尝试重刷官方或兼容固件后再测；若单链异常可换板；多链皆失败且排除连接后重点考虑控制板或批量硬件问题 | [ 0.523162@0] clkmsr ffd18004.meson_clk_msr: failed to get msr ring reg0 [ 0.641932@0] dmi: Firmware registration failed. [ 1.514706@3] Initramfs unpacking failed: junk in compressed archive [ 2.007720@1] i2c i2c-1: of_i2c: modalias failure on /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 2.011544@1] i2c i2c-1: Failed to create I2C device for /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 3.143979@2] defendkey: probe of defendkey failed with error -22 [ 3.892256@1] hub 2-0:1.0: config failed, hub doesn't have any ports! (err -19) [ 4.058196@0] thermal thermal_zone0: binding zone soc_thermal with cdev thermal-cpufreq-0 failed:-22 [ 5.682684@3] meson6-dwmac ff3f0000.ethernet eth0: fail to init PTP. 2026-04-13 04:58:57 get test_loop_securely_find_asic_num failed 2026-04-13 04:59:05 fail to write 0:1 2026-04-13 04:59:05 fail to read 0:1 | logs_10_102_1_36_MINER-10-102-1-36.txt
10.102.1.38 | 0算力 | 0.000000 | 部分算力板失效（初始化/ASIC枚举失败） | 高 | 若 SUMMARY 仍有总算力，属低算力而非零算力 | 若 SUMMARY 仍有总算力，属低算力而非零算力 | 断电后检查故障算力板与控制板之间的电源线、数据线是否插紧、有无氧化；将故障板与正常板互换槽位或交叉到另一台同型号矿机，判断是板卡还是接口/控制板问题；在 LuxOS 中对异常板尝试手动复位或重新上电（若界面支持）；若多次 enumeration 后仍被永久关闭，按硬件损坏流程送修或更换算力板 | 2026-04-13T04:59:36.188876Z [ERROR] Initialization of hashboard failed 2026-04-13T04:59:36.196649Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-13T04:59:36.626499Z [ERROR] Initialization of hashboard failed 2026-04-13T04:59:36.707480Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-13T04:59:37.118495Z [ERROR] Initialization of hashboard failed 2026-04-13T04:59:37.213132Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-13T04:59:42.590497Z [ERROR] Initialization of hashboard failed 2026-04-13T04:59:42.672008Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-13T04:59:43.126464Z [ERROR] Initialization of hashboard failed 2026-04-13T04:59:43.179701Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-13T04:59:43.618495Z [ERROR] Initialization of hashboard failed 2026-04-13T04:59:43.686128Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] | logs_10_102_1_38_MINER-10-102-1-38.txt
10.102.1.41 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T02:40:36.539440Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:45.601388Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:42:53.872765Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:44:05.387662Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:55:02.809725Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:56:11.882618Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:57:15.857200Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:58:24.913388Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:00:16.568811Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:25.631242Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:03:09.738494Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:04:18.799280Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_41_MINER-10-102-1-41.txt
10.102.1.44 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-12T01:28:04.431374Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:33:35.375406Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:37:50.000090Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T14:34:57.246640Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T14:36:06.179846Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T20:37:05.120892Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T20:38:26.041203Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:20:22.517252Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:21:42.082836Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:24:04.616680Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:26:15.171824Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:37:14.763139Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_44_MINER-10-102-1-44.txt
10.102.1.46 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；电源异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:25.167850Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:34.730288Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:04:10.193167Z [ERROR] Tuner error: {ERR:H2} Stage 14: Zero MCR on hashboards [Address(1)] 2026-04-13T02:29:00.952660Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(1)] 2026-04-13T02:40:59.290232Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:42:10.965816Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:06:40.934241Z [ERROR] Tuner error: {ERR:H2} Stage 4: Zero MCR on hashboards [Address(1)] 2026-04-13T03:21:40.819562Z [ERROR] Tuner error: {ERR:H2} Stage 4: Zero MCR on hashboards [Address(1)] 2026-04-13T03:33:29.380954Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:34:42.134627Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T04:35:42.167067Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T04:36:50.098018Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_46_MINER-10-102-1-46.txt
10.102.1.58 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T03:57:40.680911Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T03:58:48.440248Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 9 (expected: 0x1366 received: 0x1f7f) 2026-04-13T05:00:36.367246Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:01:47.926055Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 19 of read_register(reg=0x0) doesn't match chip count 110: reply 0x14 missing 2026-04-13T05:03:14.989696Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:04:24.311126Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 9 (expected: 0x1366 received: 0xe06) 2026-04-13T05:05:37.549461Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x0) 2026-04-13T05:06:45.246451Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:17:44.633431Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T05:18:57.901575Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 9 (expected: 0x1366 received: 0xc10) 2026-04-13T06:19:57.132840Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T06:21:08.652147Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 20 (expected: 0x1366 received: 0x0) | logs_10_102_1_58_MINER-10-102-1-58.txt
10.102.1.60 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:50.018908Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:59.072978Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:17.888864Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:38:37.723303Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:49:35.985169Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:50:43.410387Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:56:13.636698Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:22.694155Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:41.497298Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:00:01.340103Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:10:59.273660Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:12:06.690143Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_60_MINER-10-102-1-60.txt
10.102.1.64 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-13T01:34:36.122588Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:44.843033Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:13.564552Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:38:43.537863Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:49:44.243395Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:50:51.943488Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:56:11.595965Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:20.629748Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:45.929957Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:00:08.642893Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:11:07.712727Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:12:19.186399Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_64_MINER-10-102-1-64.txt
10.102.1.65 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-13T02:11:33.960126Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T02:12:47.937910Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T02:12:47.947028Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T02:40:48.324962Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T02:40:48.334386Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T02:42:04.324996Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T02:42:04.339291Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T02:43:18.691908Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T02:43:18.705246Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T02:44:32.067011Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T02:44:32.076295Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T02:55:39.412617Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_1_65_MINER-10-102-1-65.txt

## 低算力
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.159 | 低算力(<50TH/s) | 35.063996 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-07T21:10:08.476864Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T21:15:16.995517Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:18.878485Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:06:02.077325Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:20:36.462137Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:16:12.772087Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:36.726948Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:33:21.335733Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:30.532566Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:36:12.111990Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-12T07:38:31.749507Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-12T08:46:39.169679Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_159_MINER-10-102-0-159.txt
10.102.0.166 | 低算力(<50TH/s) | 43.215888 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-12T00:27:01.002994Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:33:19.624106Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:36.223233Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:37:16.111376Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T07:39:07.376087Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T07:50:27.991553Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:51:40.070002Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:52:40.959476Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:53:50.025441Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T14:54:49.093063Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T14:56:00.944800Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T21:01:00.048485Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_166_MINER-10-102-0-166.txt
10.102.0.182 | 低算力(<50TH/s) | 0.001222 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-10T19:40:04.350406Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T02:37:03.987857Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T02:38:13.036699Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T08:39:10.954245Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T08:40:23.528237Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:16:25.706695Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:37.226853Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:19:39.664244Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-11T10:21:06.231500Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-11T10:32:23.028846Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:33:32.588556Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T11:34:32.142730Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_182_MINER-10-102-0-182.txt
10.102.0.200 | 低算力(<50TH/s) | 46.185520 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-13T07:33:35.869363Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:37.466695Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:39.059477Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:40.656954Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:42.254320Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:43.856565Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:45.449510Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:47.047237Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:48.649230Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:50.246648Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:51.839474Z [WARN] Temperature Sensor Read Failed 2026-04-13T07:33:53.439487Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_200_MINER-10-102-0-200.txt
10.102.0.202 | 低算力(<50TH/s) | 41.786389 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-06T21:29:27.232212Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T08:26:08.872240Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T21:15:41.828549Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:20.537659Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:22:09.947989Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:16:16.281813Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:43.069362Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:59:00.763612Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:49:42.396598Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(3)] 2026-04-12T07:51:08.061955Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:52:09.881748Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T23:22:48.567949Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_202_MINER-10-102-0-202.txt
10.102.0.222 | 低算力(<50TH/s) | 40.143830 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2018-03-09T12:36:25.718243Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:26.814643Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:26.939383Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:26.984231Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2018-03-09T12:36:27.912710Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:29.507489Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:31.102627Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:32.695286Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:33.340623Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:33.353505Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2018-03-09T12:36:34.290202Z [WARN] Temperature Sensor Read Failed 2018-03-09T12:36:35.885202Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_222_MINER-10-102-0-222.txt
10.102.0.229 | 低算力(<50TH/s) | 48.911060 | 算力板部分失效（多块链 Dead，仅部分链工作） | 高 | 末段 [DEVS]：Dead=2，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 末段 [DEVS]：Dead=2，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 根据末段 [DEVS] 确认 Dead / Alive 链编号；断电后检查 Dead 链对应算力板数据排线与电源接头；将故障链与正常链互换槽位或交叉到同型号矿机，判断故障随板还是随槽位/控制板；仅单链或部分链工作时总算力约为额定三分之一属常见现象；矿池 Alive 不能排除板级失效；若链长期保持 Dead，更换算力板或送修；必要时导出含启动阶段的完整日志查初始化错误 | 2018-03-09T12:36:27.446583Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:27.526751Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2018-03-09T12:36:27.936897Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:28.034736Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2018-03-09T12:36:34.052247Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:34.102162Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2018-03-09T12:36:34.536324Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:34.607179Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2018-03-09T12:36:40.556232Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:40.571917Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 3/5 - asic enumeration failure] 2018-03-09T12:36:41.040345Z [ERROR] Initialization of hashboard failed 2018-03-09T12:36:41.077198Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 3/5 - asic enumeration failure] | logs_10_102_0_229_MINER-10-102-0-229.txt
10.102.0.237 | 低算力(<50TH/s) | 0.001334 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,3 | 2026-04-13T00:00:45.675467Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:50.696548Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:20.111247Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:36.444750Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-02T22:54:16.214241Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(2)] 2026-04-02T23:07:52.134770Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-02T23:25:00.239831Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-03T14:00:10.074971Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-04T06:10:46.398872Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-04T16:59:27.152655Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-04T17:20:51.686853Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-04T17:44:37.989186Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_237_MINER-10-102-0-237.txt
10.102.0.244 | 低算力(<50TH/s) | 32.295371 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-13T01:34:49.117430Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-04T19:19:12.720482Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:17.959985Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:23.200011Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:28.440665Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:33.677445Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:38.920569Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:44.160976Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:49.402023Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:54.640269Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:59.880515Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:20:05.120870Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_244_MINER-10-102-0-244.txt
10.102.1.19 | 低算力(<50TH/s) | 0.173572 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 |  | logs_10_102_1_19_MINER-10-102-1-19.txt