## 全部异常
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.126 | 0算力 | 0.000000 | 风扇异常（丢失/数量不足触发保护停机） | 高 | 风扇异常；若同一时间段后出现 ERROR_SOC_INIT，多为风扇保护后的连带失败，主因仍为风扇检测 | 若同一时间段后出现 ERROR_SOC_INIT，多为风扇保护后的连带失败，主因仍为风扇检测；风扇异常 | 根据日志确认要求风扇数量与实际检测数量（如 only find 3 < 4）；断电后检查四个风扇插头是否插紧、线序是否与控制板丝印一致，必要时对调插头判断是风扇还是接口；确认风扇转速是否异常或为 0；更换不转或信号异常的风扇；若硬件正常仍误报，检查控制板风扇检测电路；ERROR_SOC_INIT 若紧跟 fan lost，多为保护停机连带而非算力板主因 | 2026-04-14 04:01:38 load chain 0 eeprom data 2026-04-14 04:01:38 load chain 1 eeprom data 2026-04-14 04:01:39 load chain 2 eeprom data 2026-04-14 04:01:39 eeprom load ret:0 2026-04-14 04:01:39 eeprom load levels 2026-04-14 04:01:59 Error, fan lost, only find 3 (< 4) 2026-04-14 04:01:59 ERROR_FAN_LOST: fan lost 2026-04-14 04:01:59 stop_mining: fan lost 2026-04-14 04:01:59 ****power off hashboard**** 2026-04-14 04:02:00 ERROR_SOC_INIT: soc init failed! 2026-04-14 04:02:00 stop_mining: soc init failed! 2026-04-14 04:02:00 ****power off hashboard**** | logs_10_102_0_126_MINER-10-102-0-126.txt
10.102.0.130 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；电源异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T06:17:04.065592Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:18:16.148483Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:13:45.178221Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:15:18.756025Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:16:39.370140Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:19:28.787814Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:30:30.745137Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:31:53.436591Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:32:51.360466Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:34:18.785091Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:17:17.427062Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:18:30.117675Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_130_MINER-10-102-0-130.txt
10.102.0.131 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；电源异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-13T01:56:12.581667Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:21.642579Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:29.906107Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:59:41.457200Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:10:39.687533Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:11:48.726708Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:40:44.691433Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:42:03.932650Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:43:12.984118Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:44:24.501529Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:55:31.523167Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:56:54.910367Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_131_MINER-10-102-0-131.txt
10.102.0.150 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-14T03:07:00.094463Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1), Address(2), Address(3)] 2026-04-14T03:08:52.919214Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:08:52.928229Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 31 of read_register(reg=0x0) doesn't match chip count 110: reply 0x3e missing 2026-04-14T03:10:20.032497Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:10:20.041920Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 31 of read_register(reg=0x0) doesn't match chip count 110: reply 0x3e missing 2026-04-14T03:11:43.879438Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:11:43.892197Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 31 of read_register(reg=0x0) doesn't match chip count 110: reply 0x3e missing 2026-04-14T03:22:57.562485Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:22:57.571601Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 31 of read_register(reg=0x0) doesn't match chip count 110: reply 0x3e missing 2026-04-14T03:24:22.587629Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:24:22.597010Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 31 of read_register(reg=0x0) doesn't match chip count 110: reply 0x3e missing 2026-04-14T04:01:10.134658Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_0_150_MINER-10-102-0-150.txt
10.102.0.151 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-14T04:15:21.557166Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T04:15:21.566318Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T04:16:31.390940Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T04:16:31.403931Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T05:17:37.321737Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T05:17:37.330723Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T05:18:50.156902Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T05:18:50.166202Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T19:17:37.725097Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T19:17:37.734719Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T19:19:01.513022Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T19:19:01.522508Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_151_MINER-10-102-0-151.txt
10.102.0.155 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:2 | 2026-04-14T07:28:51.440320Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:28:51.450111Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T07:30:03.035620Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:30:03.044987Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T07:31:17.012241Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:31:17.021836Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T07:42:23.249741Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:42:23.260022Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T07:43:36.535829Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:43:36.544794Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T08:44:41.723993Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:44:41.733063Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_155_MINER-10-102-0-155.txt
10.102.0.156 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-14T07:32:09.801162Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:32:09.810560Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T07:43:11.304704Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:43:11.313658Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 27 (expected: 0x1366 received: 0x41) 2026-04-14T07:44:26.290338Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:44:26.299249Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-14T08:45:31.090294Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:45:31.099306Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 27 (expected: 0x1366 received: 0x41) 2026-04-14T08:46:44.041226Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:46:44.050220Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 27 (expected: 0x1366 received: 0x41) 2026-04-14T03:08:17.411840Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:08:17.421180Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_156_MINER-10-102-0-156.txt
10.102.0.157 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-14T07:28:56.199254Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:28:56.208089Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 5 (expected: 0x1366 received: 0x0) 2026-04-14T07:30:16.619923Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:30:16.629148Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 5 (expected: 0x1366 received: 0x1) 2026-04-14T07:31:31.677184Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:31:31.686472Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 6 (expected: 0x1366 received: 0x0) 2026-04-14T07:42:43.328967Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:42:43.337780Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 6 (expected: 0x1366 received: 0x0) 2026-04-14T07:43:56.476243Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:43:56.485100Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 5 (expected: 0x1366 received: 0x0) 2026-04-14T08:45:08.703107Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:45:08.712293Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 5 (expected: 0x1366 received: 0x400) | logs_10_102_0_157_MINER-10-102-0-157.txt
10.102.0.159 | 低算力(<50TH/s) | 36.823577 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-07T21:10:08.476864Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T21:15:16.995517Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:18.878485Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:06:02.077325Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:20:36.462137Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:16:12.772087Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:36.726948Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:33:21.335733Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:30.532566Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:36:12.111990Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-12T07:38:31.749507Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-12T08:46:39.169679Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_159_MINER-10-102-0-159.txt
10.102.0.166 | 低算力(<50TH/s) | 29.083328 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-12T00:27:01.002994Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:33:19.624106Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:36.223233Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:37:16.111376Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T07:39:07.376087Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T07:50:27.991553Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:51:40.070002Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:52:40.959476Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:53:50.025441Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T14:54:49.093063Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T14:56:00.944800Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T21:01:00.048485Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_166_MINER-10-102-0-166.txt
10.102.0.170 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；电源异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T20:33:41.310934Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:35:41.865869Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T02:58:01.897943Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T02:59:10.954817Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:24:27.449022Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:25:36.503633Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:26:44.763628Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:27:56.271312Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:38:27.963592Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:39:37.013610Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:40:45.269293Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:41:56.769274Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_170_MINER-10-102-0-170.txt
10.102.0.178 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-14T03:25:42.087910Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:27:47.535555Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:29:07.848664Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:38:29.136812Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:39:52.586482Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:42:02.311356Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:43:21.164936Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:54:19.925743Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:55:38.976254Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:00:14.413460Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:01:34.513050Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:03:47.884064Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_178_MINER-10-102-0-178.txt
10.102.0.182 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T19:15:18.338579Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T23:09:41.411167Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-13T23:23:33.895178Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(2)] 2026-04-14T03:38:31.111140Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:39:42.714016Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:59:55.262572Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:01:06.871828Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:27:42.023612Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:28:53.626334Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T19:40:04.350406Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T02:37:03.987857Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T02:38:13.036699Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_182_MINER-10-102-0-182.txt
10.102.0.184 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-14T07:43:42.010034Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:43:42.019067Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T08:44:49.423528Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:44:49.437565Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T08:46:03.001345Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:46:03.014372Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:07:14.567628Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:07:14.576877Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 51 of read_register(reg=0x0) doesn't match chip count 110: reply 0x66 missing 2026-04-14T03:08:27.494140Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:08:27.503611Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:09:40.425398Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:09:40.434638Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_184_MINER-10-102-0-184.txt
10.102.0.186 | 0算力 | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 电源异常；网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；日志同时有 PSU 协议检测失败：常在解决 EEPROM/板卡后复测；若仍存在再单独排查 PSU 与供电线 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；日志同时有 PSU 协议检测失败：常在解决 EEPROM/板卡后复测；若仍存在再单独排查 PSU 与供电线；电源异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权 | 2026-04-14T10:10:34.810691Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:10:44.426068Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:10:54.038381Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:11:03.649135Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:11:13.265145Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:11:22.879954Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:11:32.494982Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:11:42.111384Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:11:51.729746Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:12:01.341389Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:12:10.954685Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:12:20.580694Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded | logs_10_102_0_186_MINER-10-102-0-186.txt
10.102.0.195 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-13T01:44:31.005610Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:22.244241Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:47.456785Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:35:04.609146Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-13T02:46:33.544173Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:49:41.242433Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:31:22.678412Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:32:44.484393Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:34:09.610057Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:35:17.806584Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T13:25:20.821520Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 1460 chips, expected maximum 110 chips on one chain 2026-04-13T13:26:48.251497Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_195_MINER-10-102-0-195.txt
10.102.0.200 | 低算力(<50TH/s) | 47.365630 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-14T07:48:26.571856Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:28.171886Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:29.764731Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:31.366765Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:32.964102Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:34.561675Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:36.154430Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:37.754306Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:39.354160Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:40.949593Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:42.549276Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:44.144364Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_200_MINER-10-102-0-200.txt
10.102.0.202 | 低算力(<50TH/s) | 48.504846 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-06T21:29:27.232212Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T08:26:08.872240Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T21:15:41.828549Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:20.537659Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:22:09.947989Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:16:16.281813Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:43.069362Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:59:00.763612Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:49:42.396598Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(3)] 2026-04-12T07:51:08.061955Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:52:09.881748Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T23:22:48.567949Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_202_MINER-10-102-0-202.txt
10.102.0.212 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T19:15:16.392516Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:17:12.055366Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:19:58.531781Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:31:14.905245Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:32:36.746724Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:33:35.585054Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:35:03.522322Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T02:58:02.317375Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T02:59:09.750479Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:38:35.825222Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:39:44.871789Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:40:53.142202Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_212_MINER-10-102-0-212.txt
10.102.0.215 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；电源异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2 | 2026-04-14T03:43:31.312428Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:45:11.406335Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:46:10.003115Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T03:47:28.105133Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T04:00:40.603387Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:01:51.600947Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:02:54.149157Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T04:04:15.911878Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T04:16:04.212025Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:17:12.087582Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:18:44.204903Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:20:24.292387Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_215_MINER-10-102-0-215.txt
10.102.0.217 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-14T05:18:22.885076Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:19:36.046715Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:11:55.299960Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:13:06.815014Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:14:32.988446Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T06:16:18.506480Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T06:27:32.968544Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:28:42.018018Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:27:19.342328Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:28:28.392231Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:29:48.666163Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:31:14.693241Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_217_MINER-10-102-0-217.txt
10.102.0.219 | 0算力 | 0.000000 | 未识别明确故障关键词 | 低 |  |  | 建议人工复核完整日志；优先执行供电、线缆、算力板三项基础排查 | "Status": "Alive", "Status": "Dead", "Get Failures": 0, "Hardware Errors": 0, "Remote Failures": 0, "Hardware Error MHS 15m": 0.0, "Hardware Errors": 0, "Get Failures": 0, "Remote Failures": 0, "Strategy": "Failover" | logs_10_102_0_219_MINER-10-102-0-219.txt
10.102.0.221 | 0算力 | 0.000000 | 温度传感器通信失败（误报超温/温差保护停机） | 高 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-14T10:06:53.359989Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:06:54.961731Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:06:56.558940Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:06:58.156242Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:06:59.751167Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:01.350906Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:02.945885Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:04.543190Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:06.140355Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:07.739795Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:09.334766Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:10.932310Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_221_MINER-10-102-0-221.txt
10.102.0.222 | 低算力(<50TH/s) | 40.337120 | 算力板部分失效（多块链 Dead，仅部分链工作） | 高 | 末段 [DEVS]：Dead=1，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 末段 [DEVS]：Dead=1，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 根据末段 [DEVS] 确认 Dead / Alive 链编号；断电后检查 Dead 链对应算力板数据排线与电源接头；将故障链与正常链互换槽位或交叉到同型号矿机，判断故障随板还是随槽位/控制板；仅单链或部分链工作时总算力约为额定三分之一属常见现象；矿池 Alive 不能排除板级失效；若链长期保持 Dead，更换算力板或送修；必要时导出含启动阶段的完整日志查初始化错误 | 2026-04-14T07:26:36.684930Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:36.719744Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-14T07:26:43.182493Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:43.190608Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-14T07:26:49.682574Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:49.762999Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 3/5 - asic enumeration failure] 2026-04-14T07:26:56.190541Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:56.243588Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 4/5 - asic enumeration failure] 2026-04-14T07:27:02.690555Z [ERROR] Initialization of hashboard failed 2026-04-14T07:27:02.715823Z [WARN] Switching off the board; no automatic start scheduled, this board will remain offline [enumeration_reboot, 5/5 - asic enumeration failure] "Status": "Alive", "Status": "Dead", | logs_10_102_0_222_MINER-10-102-0-222.txt
10.102.0.224 | 低算力(<50TH/s) | 4.002443 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-14T04:03:32.672252Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I2} detected 1001 chips, expected maximum 110 chips on one chain 2026-04-14T07:29:29.173664Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T20:10:03.234943Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T20:11:23.189094Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:20:33.220584Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:21:56.686269Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain ========== errors（错误） ========== 2026-04-12T15:21:35.338984Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-12T15:23:04.451071Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-12T15:25:28.661659Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-12T15:29:21.974566Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-12T15:35:39.469307Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) | logs_10_102_0_224_MINER-10-102-0-224.txt
10.102.0.228 | 低算力(<50TH/s) | 43.980190 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-14T07:26:36.650495Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:36.725077Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-14T07:26:37.136237Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:37.232014Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-14T07:26:43.248244Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:43.299297Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-14T07:26:43.562640Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:26:43.636212Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:43.703721Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-14T07:26:49.848251Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:49.876193Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 3/5 - asic enumeration failure] 2026-04-14T07:26:50.340223Z [ERROR] Initialization of hashboard failed | logs_10_102_0_228_MINER-10-102-0-228.txt
10.102.0.229 | 低算力(<50TH/s) | 47.655430 | 算力板部分失效（多块链 Dead，仅部分链工作） | 高 | 末段 [DEVS]：Dead=2，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 末段 [DEVS]：Dead=2，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 根据末段 [DEVS] 确认 Dead / Alive 链编号；断电后检查 Dead 链对应算力板数据排线与电源接头；将故障链与正常链互换槽位或交叉到同型号矿机，判断故障随板还是随槽位/控制板；仅单链或部分链工作时总算力约为额定三分之一属常见现象；矿池 Alive 不能排除板级失效；若链长期保持 Dead，更换算力板或送修；必要时导出含启动阶段的完整日志查初始化错误 | 2026-04-14T07:26:37.100033Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:37.182345Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-14T07:26:37.675461Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:37.689622Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-14T07:26:43.599441Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:43.661859Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-14T07:26:44.075428Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:44.167241Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-14T07:26:50.111435Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:50.147251Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 3/5 - asic enumeration failure] 2026-04-14T07:26:50.687458Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:50.754044Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 3/5 - asic enumeration failure] | logs_10_102_0_229_MINER-10-102-0-229.txt
10.102.0.237 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；电源异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,3 | 2026-04-13T00:00:45.675467Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:50.696548Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:20.111247Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:36.444750Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:13:46.623357Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T23:22:17.160386Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T00:10:38.467565Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-14T02:07:50.162440Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:38:30.058304Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:00:49.728436Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:14:51.941871Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:17:49.841051Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_237_MINER-10-102-0-237.txt
10.102.0.244 | 低算力(<50TH/s) | 35.987642 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-13T01:34:49.117430Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:16:07.021018Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:02:58.285380Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:28:33.165529Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-04T19:19:12.720482Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:17.959985Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:23.200011Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:28.440665Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:33.677445Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:38.920569Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:44.160976Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:49.402023Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_244_MINER-10-102-0-244.txt
10.102.0.249 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T16:05:11.363375Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:14:00.124149Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:15:28.333564Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:18:27.816434Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:20:03.264115Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:31:06.797668Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:32:40.005811Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:33:42.577777Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:35:20.103176Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T02:36:22.669073Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T02:37:42.007741Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:06:33.489608Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_249_MINER-10-102-0-249.txt
10.102.1.13 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-14T03:08:37.199953Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:09:43.638832Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:16:34.385224Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:17:43.081027Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:18:52.131596Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:20:05.780161Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:24:27.447989Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:25:36.518594Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:26:44.753128Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:27:56.295838Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:38:27.936804Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:39:36.997689Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_13_MINER-10-102-1-13.txt
10.102.1.14 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；电源异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-14T03:54:16.873732Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:01:46.566576Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:02:55.619189Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:04:03.932182Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:05:22.129480Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:16:19.558589Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:17:28.605997Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:18:29.317850Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:19:40.836141Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:58:25.539557Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:00:15.829560Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:24.877453Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_14_MINER-10-102-1-14.txt
10.102.1.15 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-13T01:58:50.290062Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:42.696150Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:42:53.294206Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:03.542514Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:03:13.918412Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:04:33.775062Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:09:36.486679Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:17:08.099340Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:20:00.928527Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T00:00:53.326086Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T00:04:40.760077Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T01:03:52.902014Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] | logs_10_102_1_15_MINER-10-102-1-15.txt
10.102.1.19 | 低算力(<50TH/s) | 0.143891 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；电源异常；算力板/芯片异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；电源异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 |  | logs_10_102_1_19_MINER-10-102-1-19.txt
10.102.1.1 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T03:59:25.630682Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T10:00:25.173710Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T10:01:36.674554Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T16:51:56.640708Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T16:53:10.452722Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:13:47.048127Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:15:10.498008Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:17:04.819960Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:18:19.399241Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:29:30.494690Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:30:54.691948Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:31:57.218423Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_1_MINER-10-102-1-1.txt
10.102.1.21 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-14T05:18:33.877510Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:58.685998Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:43:06.100010Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:44:19.285996Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:55:22.132594Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:56:29.803797Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:57:38.605734Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:58:50.049911Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:00:24.534006Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:38.517412Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:03:09.729862Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:04:18.788263Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_21_MINER-10-102-1-21.txt
10.102.1.29 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时 | 算力板/芯片异常；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1 | 2026-04-13T12:27:42.145457Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:13:52.174618Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:15:10.733394Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:18:33.992828Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:20:14.275744Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:31:33.245803Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:33:39.370870Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T20:34:56.415322Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:36:16.738898Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T02:58:02.364962Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:01:21.137157Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T03:38:29.122526Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_29_MINER-10-102-1-29.txt
10.102.1.2 | 低算力(<50TH/s) | 0.159910 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-10T02:35:39.792621Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:51.332943Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:05:23.669483Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:06:32.485487Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:21:36.102303Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:22:55.855540Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T21:47:53.028271Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-11T10:16:26.017922Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:37.577353Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:45:00.397577Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-12T23:20:32.371572Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:22:03.581055Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_2_MINER-10-102-1-2.txt
10.102.1.36 | 0算力 | 0.000000 | 矿机服务异常/接口超时 | 高 |  |  | 重启矿机服务或整机重启；检查控制板负载和系统日志；确认管理端口未被占用 | [ 0.523556@3] clkmsr ffd18004.meson_clk_msr: failed to get msr ring reg0 [ 0.634648@3] dmi: Firmware registration failed. [ 1.506034@1] Initramfs unpacking failed: junk in compressed archive [ 2.000527@3] i2c i2c-1: of_i2c: modalias failure on /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 2.004317@3] i2c i2c-1: Failed to create I2C device for /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 3.136328@2] defendkey: probe of defendkey failed with error -22 [ 3.884611@1] hub 2-0:1.0: config failed, hub doesn't have any ports! (err -19) [ 4.050408@0] thermal thermal_zone0: binding zone soc_thermal with cdev thermal-cpufreq-0 failed:-22 [ 5.672286@0] meson6-dwmac ff3f0000.ethernet eth0: fail to init PTP. "Hardware Errors": 0, "Get Failures": 0, "Remote Failures": 0, | logs_10_102_1_36_MINER-10-102-1-36.txt
10.102.1.38 | 0算力 | 0.000000 | 矿池/Stratum连接不稳定（频繁断连） | 高 | 算力板 Dead/低温常为未持续获得任务所致，先稳定矿池连接再判硬件 | 算力板 Dead/低温常为未持续获得任务所致，先稳定矿池连接再判硬件 | 检查矿机到矿池域名的网络：延迟、丢包、DNS（可 ping / traceroute / 换 DNS 对比）；检查交换机端口、网线、上联链路；排除同网段广播风暴或限速；在 LuxOS 中切换备用矿池或矿池线路，排除矿池侧短暂故障；重启矿机或重载 Stratum 连接后观察 Accepted 与算力是否恢复；核对矿池子账户与矿工名；若仍频繁断连可尝试升级/回退 Luxminer 固件对比 | 2026-04-14T03:58:46.273652Z [ERROR] connection dropped due to pool inactivity 2026-04-14T03:58:46.273860Z [ERROR] Stratum read failure 2026-04-14T03:58:46.274472Z [INFO] Connection closed by the server 2026-04-14T04:01:01.535428Z [INFO] Connection closed by the server 2026-04-14T04:09:32.744969Z [ERROR] connection dropped due to pool inactivity 2026-04-14T04:09:32.745171Z [ERROR] Stratum read failure 2026-04-14T04:09:32.745839Z [INFO] Connection closed by the server 2026-04-14T04:11:18.622989Z [INFO] Connection closed by the server 2026-04-14T04:20:44.942831Z [ERROR] connection dropped due to pool inactivity 2026-04-14T04:20:44.944403Z [ERROR] Stratum read failure 2026-04-14T04:20:44.945031Z [INFO] Connection closed by the server 2026-04-14T04:21:29.914512Z [INFO] Connection closed by the server | logs_10_102_1_38_MINER-10-102-1-38.txt
10.102.1.41 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-14T03:54:02.746357Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:01:45.115092Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:02:54.168651Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:04:02.451801Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:05:13.989926Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:16:11.991221Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:17:21.047144Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:18:25.014413Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:19:34.064791Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:11:53.714336Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:13:02.777147Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:14:11.058881Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_41_MINER-10-102-1-41.txt
10.102.1.44 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T19:04:30.717709Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:13:41.268540Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:15:08.216644Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:17:39.798389Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:20:06.920412Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:31:06.981598Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:32:26.918097Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:33:26.985490Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:35:34.405748Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:06:17.765477Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:07:24.136151Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:08:30.495842Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_44_MINER-10-102-1-44.txt
10.102.1.46 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-14T03:16:34.476622Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:17:43.153540Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:18:52.211330Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:20:05.895525Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:24:27.524087Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:25:36.586910Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:26:44.811629Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:27:56.288940Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:38:27.940127Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:39:37.002021Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:40:45.254692Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:42:03.281712Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_46_MINER-10-102-1-46.txt
10.102.1.58 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-14T04:01:43.934244Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T04:02:57.157280Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I1} unexpected revision of chip 3 (expected: 0x1366 received: 0x1fff) 2026-04-14T04:04:04.594870Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T04:15:02.022726Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T04:16:11.200395Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T05:17:16.936481Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T05:18:24.369779Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T06:12:33.721609Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T06:13:42.892657Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T06:14:51.023956Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I1} unexpected revision of chip 5 (expected: 0x1366 received: 0x0) 2026-04-14T06:16:02.597805Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T06:27:01.021813Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_58_MINER-10-102-1-58.txt
10.102.1.59 | 低算力(<50TH/s) | 47.809600 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,3 | 2026-04-10T23:16:34.685589Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:18:19.532950Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T12:10:21.954887Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T12:11:30.907960Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:05.253515Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-12T07:37:57.811006Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-12T23:23:00.354405Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:24:19.565920Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:06.426416Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:15.979449Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:16:23.328355Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-04-13T19:17:44.536601Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_59_MINER-10-102-1-59.txt
10.102.1.60 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T19:31:38.020843Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:32:38.722647Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:34:01.439462Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:06:24.370087Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:07:30.796306Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:08:37.200146Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:10:10.673724Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:16:34.361093Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:17:43.035210Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:18:52.077755Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:20:10.943796Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:24:33.799682Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_60_MINER-10-102-1-60.txt
10.102.1.64 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-14T08:41:33.105411Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:36.122588Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:44.843033Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:13.564552Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:38:43.537863Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:49:44.243395Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:50:51.943488Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:56:11.595965Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:20.629748Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:45.929957Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:00:08.642893Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:11:07.712727Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_64_MINER-10-102-1-64.txt
10.102.1.65 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-14T04:16:08.292824Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T04:16:08.302190Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x0) 2026-04-14T04:17:22.342727Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T04:17:22.351775Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x0) 2026-04-14T05:18:27.416067Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T05:18:27.425006Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0xd3c) 2026-04-14T05:19:40.172658Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T05:19:40.181661Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x50) 2026-04-14T06:12:11.280917Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T06:12:11.290418Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0xdd0) 2026-04-14T06:13:27.347157Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T06:13:27.360240Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x2c0) | logs_10_102_1_65_MINER-10-102-1-65.txt

## 0算力
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.126 | 0算力 | 0.000000 | 风扇异常（丢失/数量不足触发保护停机） | 高 | 风扇异常；若同一时间段后出现 ERROR_SOC_INIT，多为风扇保护后的连带失败，主因仍为风扇检测 | 若同一时间段后出现 ERROR_SOC_INIT，多为风扇保护后的连带失败，主因仍为风扇检测；风扇异常 | 根据日志确认要求风扇数量与实际检测数量（如 only find 3 < 4）；断电后检查四个风扇插头是否插紧、线序是否与控制板丝印一致，必要时对调插头判断是风扇还是接口；确认风扇转速是否异常或为 0；更换不转或信号异常的风扇；若硬件正常仍误报，检查控制板风扇检测电路；ERROR_SOC_INIT 若紧跟 fan lost，多为保护停机连带而非算力板主因 | 2026-04-14 04:01:38 load chain 0 eeprom data 2026-04-14 04:01:38 load chain 1 eeprom data 2026-04-14 04:01:39 load chain 2 eeprom data 2026-04-14 04:01:39 eeprom load ret:0 2026-04-14 04:01:39 eeprom load levels 2026-04-14 04:01:59 Error, fan lost, only find 3 (< 4) 2026-04-14 04:01:59 ERROR_FAN_LOST: fan lost 2026-04-14 04:01:59 stop_mining: fan lost 2026-04-14 04:01:59 ****power off hashboard**** 2026-04-14 04:02:00 ERROR_SOC_INIT: soc init failed! 2026-04-14 04:02:00 stop_mining: soc init failed! 2026-04-14 04:02:00 ****power off hashboard**** | logs_10_102_0_126_MINER-10-102-0-126.txt
10.102.0.130 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；电源异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T06:17:04.065592Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:18:16.148483Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:13:45.178221Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:15:18.756025Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:16:39.370140Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:19:28.787814Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:30:30.745137Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:31:53.436591Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:32:51.360466Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:34:18.785091Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:17:17.427062Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:18:30.117675Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_130_MINER-10-102-0-130.txt
10.102.0.131 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；电源异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-13T01:56:12.581667Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:21.642579Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:29.906107Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:59:41.457200Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:10:39.687533Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:11:48.726708Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:40:44.691433Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:42:03.932650Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:43:12.984118Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:44:24.501529Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:55:31.523167Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:56:54.910367Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_131_MINER-10-102-0-131.txt
10.102.0.150 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-14T03:07:00.094463Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1), Address(2), Address(3)] 2026-04-14T03:08:52.919214Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:08:52.928229Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 31 of read_register(reg=0x0) doesn't match chip count 110: reply 0x3e missing 2026-04-14T03:10:20.032497Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:10:20.041920Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 31 of read_register(reg=0x0) doesn't match chip count 110: reply 0x3e missing 2026-04-14T03:11:43.879438Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:11:43.892197Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 31 of read_register(reg=0x0) doesn't match chip count 110: reply 0x3e missing 2026-04-14T03:22:57.562485Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:22:57.571601Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 31 of read_register(reg=0x0) doesn't match chip count 110: reply 0x3e missing 2026-04-14T03:24:22.587629Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:24:22.597010Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 31 of read_register(reg=0x0) doesn't match chip count 110: reply 0x3e missing 2026-04-14T04:01:10.134658Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_0_150_MINER-10-102-0-150.txt
10.102.0.151 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-14T04:15:21.557166Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T04:15:21.566318Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T04:16:31.390940Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T04:16:31.403931Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T05:17:37.321737Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T05:17:37.330723Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T05:18:50.156902Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T05:18:50.166202Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T19:17:37.725097Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T19:17:37.734719Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-13T19:19:01.513022Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-13T19:19:01.522508Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_151_MINER-10-102-0-151.txt
10.102.0.155 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:2 | 2026-04-14T07:28:51.440320Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:28:51.450111Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T07:30:03.035620Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:30:03.044987Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T07:31:17.012241Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:31:17.021836Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T07:42:23.249741Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:42:23.260022Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T07:43:36.535829Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:43:36.544794Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T08:44:41.723993Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:44:41.733063Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_155_MINER-10-102-0-155.txt
10.102.0.156 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-14T07:32:09.801162Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:32:09.810560Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T07:43:11.304704Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:43:11.313658Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 27 (expected: 0x1366 received: 0x41) 2026-04-14T07:44:26.290338Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:44:26.299249Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-14T08:45:31.090294Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:45:31.099306Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 27 (expected: 0x1366 received: 0x41) 2026-04-14T08:46:44.041226Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:46:44.050220Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 27 (expected: 0x1366 received: 0x41) 2026-04-14T03:08:17.411840Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:08:17.421180Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_156_MINER-10-102-0-156.txt
10.102.0.157 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-14T07:28:56.199254Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:28:56.208089Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 5 (expected: 0x1366 received: 0x0) 2026-04-14T07:30:16.619923Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:30:16.629148Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 5 (expected: 0x1366 received: 0x1) 2026-04-14T07:31:31.677184Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:31:31.686472Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 6 (expected: 0x1366 received: 0x0) 2026-04-14T07:42:43.328967Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:42:43.337780Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 6 (expected: 0x1366 received: 0x0) 2026-04-14T07:43:56.476243Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:43:56.485100Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 5 (expected: 0x1366 received: 0x0) 2026-04-14T08:45:08.703107Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:45:08.712293Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 5 (expected: 0x1366 received: 0x400) | logs_10_102_0_157_MINER-10-102-0-157.txt
10.102.0.170 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；电源异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T20:33:41.310934Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:35:41.865869Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T02:58:01.897943Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T02:59:10.954817Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:24:27.449022Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:25:36.503633Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:26:44.763628Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:27:56.271312Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:38:27.963592Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:39:37.013610Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:40:45.269293Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:41:56.769274Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_170_MINER-10-102-0-170.txt
10.102.0.178 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-14T03:25:42.087910Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:27:47.535555Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:29:07.848664Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:38:29.136812Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:39:52.586482Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:42:02.311356Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:43:21.164936Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:54:19.925743Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:55:38.976254Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:00:14.413460Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:01:34.513050Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:03:47.884064Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_178_MINER-10-102-0-178.txt
10.102.0.182 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T19:15:18.338579Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T23:09:41.411167Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-13T23:23:33.895178Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(2)] 2026-04-14T03:38:31.111140Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:39:42.714016Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:59:55.262572Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:01:06.871828Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:27:42.023612Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:28:53.626334Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T19:40:04.350406Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T02:37:03.987857Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T02:38:13.036699Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_182_MINER-10-102-0-182.txt
10.102.0.184 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-14T07:43:42.010034Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:43:42.019067Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T08:44:49.423528Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:44:49.437565Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T08:46:03.001345Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:46:03.014372Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:07:14.567628Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:07:14.576877Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 51 of read_register(reg=0x0) doesn't match chip count 110: reply 0x66 missing 2026-04-14T03:08:27.494140Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:08:27.503611Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:09:40.425398Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T03:09:40.434638Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_184_MINER-10-102-0-184.txt
10.102.0.186 | 0算力 | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 电源异常；网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；日志同时有 PSU 协议检测失败：常在解决 EEPROM/板卡后复测；若仍存在再单独排查 PSU 与供电线 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；日志同时有 PSU 协议检测失败：常在解决 EEPROM/板卡后复测；若仍存在再单独排查 PSU 与供电线；电源异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权 | 2026-04-14T10:10:34.810691Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:10:44.426068Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:10:54.038381Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:11:03.649135Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:11:13.265145Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:11:22.879954Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:11:32.494982Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:11:42.111384Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:11:51.729746Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:12:01.341389Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:12:10.954685Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-14T10:12:20.580694Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded | logs_10_102_0_186_MINER-10-102-0-186.txt
10.102.0.195 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-13T01:44:31.005610Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:22.244241Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:47.456785Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:35:04.609146Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-13T02:46:33.544173Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:49:41.242433Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:31:22.678412Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:32:44.484393Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:34:09.610057Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T06:35:17.806584Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T13:25:20.821520Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 1460 chips, expected maximum 110 chips on one chain 2026-04-13T13:26:48.251497Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_195_MINER-10-102-0-195.txt
10.102.0.212 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-13T19:15:16.392516Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:17:12.055366Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:19:58.531781Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:31:14.905245Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:32:36.746724Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:33:35.585054Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:35:03.522322Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T02:58:02.317375Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T02:59:09.750479Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:38:35.825222Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:39:44.871789Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:40:53.142202Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_212_MINER-10-102-0-212.txt
10.102.0.215 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；电源异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2 | 2026-04-14T03:43:31.312428Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:45:11.406335Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:46:10.003115Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T03:47:28.105133Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T04:00:40.603387Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:01:51.600947Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:02:54.149157Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T04:04:15.911878Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T04:16:04.212025Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:17:12.087582Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:18:44.204903Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:20:24.292387Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_215_MINER-10-102-0-215.txt
10.102.0.217 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-14T05:18:22.885076Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:19:36.046715Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:11:55.299960Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:13:06.815014Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:14:32.988446Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T06:16:18.506480Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T06:27:32.968544Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:28:42.018018Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:27:19.342328Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:28:28.392231Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:29:48.666163Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:31:14.693241Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_217_MINER-10-102-0-217.txt
10.102.0.219 | 0算力 | 0.000000 | 未识别明确故障关键词 | 低 |  |  | 建议人工复核完整日志；优先执行供电、线缆、算力板三项基础排查 | "Status": "Alive", "Status": "Dead", "Get Failures": 0, "Hardware Errors": 0, "Remote Failures": 0, "Hardware Error MHS 15m": 0.0, "Hardware Errors": 0, "Get Failures": 0, "Remote Failures": 0, "Strategy": "Failover" | logs_10_102_0_219_MINER-10-102-0-219.txt
10.102.0.221 | 0算力 | 0.000000 | 温度传感器通信失败（误报超温/温差保护停机） | 高 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-14T10:06:53.359989Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:06:54.961731Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:06:56.558940Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:06:58.156242Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:06:59.751167Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:01.350906Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:02.945885Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:04.543190Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:06.140355Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:07.739795Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:09.334766Z [WARN] Temperature Sensor Read Failed 2026-04-14T10:07:10.932310Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_221_MINER-10-102-0-221.txt
10.102.0.237 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；电源异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,3 | 2026-04-13T00:00:45.675467Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:50.696548Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:20.111247Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:36.444750Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:13:46.623357Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T23:22:17.160386Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T00:10:38.467565Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-14T02:07:50.162440Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:38:30.058304Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:00:49.728436Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:14:51.941871Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:17:49.841051Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_237_MINER-10-102-0-237.txt
10.102.0.249 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T16:05:11.363375Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:14:00.124149Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:15:28.333564Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:18:27.816434Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:20:03.264115Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:31:06.797668Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:32:40.005811Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:33:42.577777Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:35:20.103176Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T02:36:22.669073Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T02:37:42.007741Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:06:33.489608Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_249_MINER-10-102-0-249.txt
10.102.1.13 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-14T03:08:37.199953Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:09:43.638832Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:16:34.385224Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:17:43.081027Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:18:52.131596Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:20:05.780161Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:24:27.447989Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:25:36.518594Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:26:44.753128Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:27:56.295838Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:38:27.936804Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:39:36.997689Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_13_MINER-10-102-1-13.txt
10.102.1.14 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；电源异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-14T03:54:16.873732Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:01:46.566576Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:02:55.619189Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:04:03.932182Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:05:22.129480Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:16:19.558589Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:17:28.605997Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:18:29.317850Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:19:40.836141Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:58:25.539557Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:00:15.829560Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:24.877453Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_14_MINER-10-102-1-14.txt
10.102.1.15 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-13T01:58:50.290062Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:42.696150Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:42:53.294206Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:03.542514Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:03:13.918412Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:04:33.775062Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:09:36.486679Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:17:08.099340Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:20:00.928527Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T00:00:53.326086Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T00:04:40.760077Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T01:03:52.902014Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] | logs_10_102_1_15_MINER-10-102-1-15.txt
10.102.1.1 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T03:59:25.630682Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T10:00:25.173710Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T10:01:36.674554Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T16:51:56.640708Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T16:53:10.452722Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:13:47.048127Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:15:10.498008Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:17:04.819960Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:18:19.399241Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:29:30.494690Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:30:54.691948Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:31:57.218423Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_1_MINER-10-102-1-1.txt
10.102.1.21 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-14T05:18:33.877510Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:41:58.685998Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:43:06.100010Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:44:19.285996Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:55:22.132594Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:56:29.803797Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:57:38.605734Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T03:58:50.049911Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:00:24.534006Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:01:38.517412Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:03:09.729862Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T05:04:18.788263Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_21_MINER-10-102-1-21.txt
10.102.1.29 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时 | 算力板/芯片异常；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1 | 2026-04-13T12:27:42.145457Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:13:52.174618Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:15:10.733394Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:18:33.992828Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:20:14.275744Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T19:31:33.245803Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:33:39.370870Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-13T20:34:56.415322Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:36:16.738898Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T02:58:02.364962Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:01:21.137157Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-14T03:38:29.122526Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_29_MINER-10-102-1-29.txt
10.102.1.36 | 0算力 | 0.000000 | 矿机服务异常/接口超时 | 高 |  |  | 重启矿机服务或整机重启；检查控制板负载和系统日志；确认管理端口未被占用 | [ 0.523556@3] clkmsr ffd18004.meson_clk_msr: failed to get msr ring reg0 [ 0.634648@3] dmi: Firmware registration failed. [ 1.506034@1] Initramfs unpacking failed: junk in compressed archive [ 2.000527@3] i2c i2c-1: of_i2c: modalias failure on /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 2.004317@3] i2c i2c-1: Failed to create I2C device for /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 3.136328@2] defendkey: probe of defendkey failed with error -22 [ 3.884611@1] hub 2-0:1.0: config failed, hub doesn't have any ports! (err -19) [ 4.050408@0] thermal thermal_zone0: binding zone soc_thermal with cdev thermal-cpufreq-0 failed:-22 [ 5.672286@0] meson6-dwmac ff3f0000.ethernet eth0: fail to init PTP. "Hardware Errors": 0, "Get Failures": 0, "Remote Failures": 0, | logs_10_102_1_36_MINER-10-102-1-36.txt
10.102.1.38 | 0算力 | 0.000000 | 矿池/Stratum连接不稳定（频繁断连） | 高 | 算力板 Dead/低温常为未持续获得任务所致，先稳定矿池连接再判硬件 | 算力板 Dead/低温常为未持续获得任务所致，先稳定矿池连接再判硬件 | 检查矿机到矿池域名的网络：延迟、丢包、DNS（可 ping / traceroute / 换 DNS 对比）；检查交换机端口、网线、上联链路；排除同网段广播风暴或限速；在 LuxOS 中切换备用矿池或矿池线路，排除矿池侧短暂故障；重启矿机或重载 Stratum 连接后观察 Accepted 与算力是否恢复；核对矿池子账户与矿工名；若仍频繁断连可尝试升级/回退 Luxminer 固件对比 | 2026-04-14T03:58:46.273652Z [ERROR] connection dropped due to pool inactivity 2026-04-14T03:58:46.273860Z [ERROR] Stratum read failure 2026-04-14T03:58:46.274472Z [INFO] Connection closed by the server 2026-04-14T04:01:01.535428Z [INFO] Connection closed by the server 2026-04-14T04:09:32.744969Z [ERROR] connection dropped due to pool inactivity 2026-04-14T04:09:32.745171Z [ERROR] Stratum read failure 2026-04-14T04:09:32.745839Z [INFO] Connection closed by the server 2026-04-14T04:11:18.622989Z [INFO] Connection closed by the server 2026-04-14T04:20:44.942831Z [ERROR] connection dropped due to pool inactivity 2026-04-14T04:20:44.944403Z [ERROR] Stratum read failure 2026-04-14T04:20:44.945031Z [INFO] Connection closed by the server 2026-04-14T04:21:29.914512Z [INFO] Connection closed by the server | logs_10_102_1_38_MINER-10-102-1-38.txt
10.102.1.41 | 0算力 | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-14T03:54:02.746357Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:01:45.115092Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:02:54.168651Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:04:02.451801Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:05:13.989926Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:16:11.991221Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:17:21.047144Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:18:25.014413Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T05:19:34.064791Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:11:53.714336Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:13:02.777147Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T06:14:11.058881Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_41_MINER-10-102-1-41.txt
10.102.1.44 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T19:04:30.717709Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:13:41.268540Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:15:08.216644Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:17:39.798389Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:20:06.920412Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:31:06.981598Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:32:26.918097Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:33:26.985490Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:35:34.405748Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:06:17.765477Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:07:24.136151Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:08:30.495842Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_44_MINER-10-102-1-44.txt
10.102.1.46 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-14T03:16:34.476622Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:17:43.153540Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:18:52.211330Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:20:05.895525Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:24:27.524087Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:25:36.586910Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:26:44.811629Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:27:56.288940Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:38:27.940127Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:39:37.002021Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:40:45.254692Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:42:03.281712Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_46_MINER-10-102-1-46.txt
10.102.1.58 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-14T04:01:43.934244Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T04:02:57.157280Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I1} unexpected revision of chip 3 (expected: 0x1366 received: 0x1fff) 2026-04-14T04:04:04.594870Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T04:15:02.022726Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T04:16:11.200395Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T05:17:16.936481Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T05:18:24.369779Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T06:12:33.721609Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T06:13:42.892657Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T06:14:51.023956Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I1} unexpected revision of chip 5 (expected: 0x1366 received: 0x0) 2026-04-14T06:16:02.597805Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T06:27:01.021813Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_58_MINER-10-102-1-58.txt
10.102.1.60 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-13T19:31:38.020843Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:32:38.722647Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T20:34:01.439462Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:06:24.370087Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:07:30.796306Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:08:37.200146Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:10:10.673724Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T03:16:34.361093Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:17:43.035210Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:18:52.077755Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:20:10.943796Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:24:33.799682Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_60_MINER-10-102-1-60.txt
10.102.1.64 | 0算力 | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-14T08:41:33.105411Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:36.122588Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:44.843033Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:37:13.564552Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:38:43.537863Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:49:44.243395Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:50:51.943488Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:56:11.595965Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:57:20.629748Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:58:45.929957Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:00:08.642893Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T02:11:07.712727Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_64_MINER-10-102-1-64.txt
10.102.1.65 | 0算力 | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-14T04:16:08.292824Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T04:16:08.302190Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x0) 2026-04-14T04:17:22.342727Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T04:17:22.351775Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x0) 2026-04-14T05:18:27.416067Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T05:18:27.425006Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0xd3c) 2026-04-14T05:19:40.172658Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T05:19:40.181661Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x50) 2026-04-14T06:12:11.280917Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T06:12:11.290418Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0xdd0) 2026-04-14T06:13:27.347157Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T06:13:27.360240Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x2c0) | logs_10_102_1_65_MINER-10-102-1-65.txt

## 低算力
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.159 | 低算力(<50TH/s) | 36.823577 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-07T21:10:08.476864Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T21:15:16.995517Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:18.878485Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:06:02.077325Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:20:36.462137Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:16:12.772087Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:36.726948Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:33:21.335733Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:30.532566Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:36:12.111990Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-12T07:38:31.749507Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-12T08:46:39.169679Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_159_MINER-10-102-0-159.txt
10.102.0.166 | 低算力(<50TH/s) | 29.083328 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-12T00:27:01.002994Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:33:19.624106Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:36.223233Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:37:16.111376Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T07:39:07.376087Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T07:50:27.991553Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:51:40.070002Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:52:40.959476Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T08:53:50.025441Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T14:54:49.093063Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T14:56:00.944800Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T21:01:00.048485Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_166_MINER-10-102-0-166.txt
10.102.0.200 | 低算力(<50TH/s) | 47.365630 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-14T07:48:26.571856Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:28.171886Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:29.764731Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:31.366765Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:32.964102Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:34.561675Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:36.154430Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:37.754306Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:39.354160Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:40.949593Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:42.549276Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:48:44.144364Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_200_MINER-10-102-0-200.txt
10.102.0.202 | 低算力(<50TH/s) | 48.504846 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-06T21:29:27.232212Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T08:26:08.872240Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T21:15:41.828549Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:20.537659Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:22:09.947989Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:16:16.281813Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:43.069362Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:59:00.763612Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:49:42.396598Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(3)] 2026-04-12T07:51:08.061955Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:52:09.881748Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T23:22:48.567949Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_202_MINER-10-102-0-202.txt
10.102.0.222 | 低算力(<50TH/s) | 40.337120 | 算力板部分失效（多块链 Dead，仅部分链工作） | 高 | 末段 [DEVS]：Dead=1，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 末段 [DEVS]：Dead=1，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 根据末段 [DEVS] 确认 Dead / Alive 链编号；断电后检查 Dead 链对应算力板数据排线与电源接头；将故障链与正常链互换槽位或交叉到同型号矿机，判断故障随板还是随槽位/控制板；仅单链或部分链工作时总算力约为额定三分之一属常见现象；矿池 Alive 不能排除板级失效；若链长期保持 Dead，更换算力板或送修；必要时导出含启动阶段的完整日志查初始化错误 | 2026-04-14T07:26:36.684930Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:36.719744Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-14T07:26:43.182493Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:43.190608Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-14T07:26:49.682574Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:49.762999Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 3/5 - asic enumeration failure] 2026-04-14T07:26:56.190541Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:56.243588Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 4/5 - asic enumeration failure] 2026-04-14T07:27:02.690555Z [ERROR] Initialization of hashboard failed 2026-04-14T07:27:02.715823Z [WARN] Switching off the board; no automatic start scheduled, this board will remain offline [enumeration_reboot, 5/5 - asic enumeration failure] "Status": "Alive", "Status": "Dead", | logs_10_102_0_222_MINER-10-102-0-222.txt
10.102.0.224 | 低算力(<50TH/s) | 4.002443 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-14T04:03:32.672252Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I2} detected 1001 chips, expected maximum 110 chips on one chain 2026-04-14T07:29:29.173664Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T20:10:03.234943Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T20:11:23.189094Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:20:33.220584Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:21:56.686269Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain ========== errors（错误） ========== 2026-04-12T15:21:35.338984Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-12T15:23:04.451071Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-12T15:25:28.661659Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-12T15:29:21.974566Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-12T15:35:39.469307Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) | logs_10_102_0_224_MINER-10-102-0-224.txt
10.102.0.228 | 低算力(<50TH/s) | 43.980190 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-14T07:26:36.650495Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:36.725077Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-14T07:26:37.136237Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:37.232014Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-14T07:26:43.248244Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:43.299297Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-14T07:26:43.562640Z [WARN] Temperature Sensor Read Failed 2026-04-14T07:26:43.636212Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:43.703721Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-14T07:26:49.848251Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:49.876193Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 3/5 - asic enumeration failure] 2026-04-14T07:26:50.340223Z [ERROR] Initialization of hashboard failed | logs_10_102_0_228_MINER-10-102-0-228.txt
10.102.0.229 | 低算力(<50TH/s) | 47.655430 | 算力板部分失效（多块链 Dead，仅部分链工作） | 高 | 末段 [DEVS]：Dead=2，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 末段 [DEVS]：Dead=2，Alive=1；多为板卡/排线/槽位问题，建议交叉换槽位与检查供电接口 | 根据末段 [DEVS] 确认 Dead / Alive 链编号；断电后检查 Dead 链对应算力板数据排线与电源接头；将故障链与正常链互换槽位或交叉到同型号矿机，判断故障随板还是随槽位/控制板；仅单链或部分链工作时总算力约为额定三分之一属常见现象；矿池 Alive 不能排除板级失效；若链长期保持 Dead，更换算力板或送修；必要时导出含启动阶段的完整日志查初始化错误 | 2026-04-14T07:26:37.100033Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:37.182345Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-14T07:26:37.675461Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:37.689622Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 1/5 - asic enumeration failure] 2026-04-14T07:26:43.599441Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:43.661859Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-14T07:26:44.075428Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:44.167241Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 2/5 - asic enumeration failure] 2026-04-14T07:26:50.111435Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:50.147251Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 3/5 - asic enumeration failure] 2026-04-14T07:26:50.687458Z [ERROR] Initialization of hashboard failed 2026-04-14T07:26:50.754044Z [WARN] Rebooting board; automatic start scheduled [enumeration_reboot, 3/5 - asic enumeration failure] | logs_10_102_0_229_MINER-10-102-0-229.txt
10.102.0.244 | 低算力(<50TH/s) | 35.987642 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-13T01:34:49.117430Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:16:07.021018Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T04:02:58.285380Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-14T07:28:33.165529Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-04T19:19:12.720482Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:17.959985Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:23.200011Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:28.440665Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:33.677445Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:38.920569Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:44.160976Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:49.402023Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_244_MINER-10-102-0-244.txt
10.102.1.19 | 低算力(<50TH/s) | 0.143891 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；电源异常；算力板/芯片异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；电源异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 |  | logs_10_102_1_19_MINER-10-102-1-19.txt
10.102.1.2 | 低算力(<50TH/s) | 0.159910 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-10T02:35:39.792621Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:51.332943Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:05:23.669483Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:06:32.485487Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:21:36.102303Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:22:55.855540Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-10T21:47:53.028271Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-11T10:16:26.017922Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:37.577353Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:45:00.397577Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-12T23:20:32.371572Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:22:03.581055Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_2_MINER-10-102-1-2.txt
10.102.1.59 | 低算力(<50TH/s) | 47.809600 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,3 | 2026-04-10T23:16:34.685589Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:18:19.532950Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T12:10:21.954887Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T12:11:30.907960Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:05.253515Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-12T07:37:57.811006Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-12T23:23:00.354405Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:24:19.565920Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:06.426416Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:15.979449Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:16:23.328355Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-04-13T19:17:44.536601Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_59_MINER-10-102-1-59.txt