## 全部异常
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.162 | 低算力(<50TH/s) | 46.767700 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-23T04:54:25.607447Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:27.200295Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:28.802620Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:30.395338Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:31.997449Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:33.592581Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:35.190051Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:36.787748Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:38.383080Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:39.985431Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:41.580488Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:43.178102Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_162_MINER-10-102-0-162.txt
10.102.0.174 | 低算力(<50TH/s) | 36.487960 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-03-29T19:43:50.469907Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-03-30T03:22:33.181202Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-03-31T18:07:16.144838Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-03-31T18:18:41.776610Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-02T05:33:24.183273Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T05:34:33.408224Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:24:43.433314Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:54:29.884466Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-02T17:17:21.178485Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-02T18:41:31.390484Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-02T19:44:31.798110Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-03T07:02:00.401209Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_174_MINER-10-102-0-174.txt
10.102.0.176 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-17T22:53:17.719013Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T22:54:38.953415Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T22:56:03.815519Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T23:07:01.243560Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T23:08:20.672504Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T00:09:20.641422Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T00:10:40.643539Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T06:49:00.607621Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T06:50:08.294628Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T07:24:16.205140Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T07:25:25.265135Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T07:26:33.516332Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_176_MINER-10-102-0-176.txt
10.102.0.178 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-20T07:30:42.423669Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:30:51.975216Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:01.501873Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:11.023161Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:20.540639Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:30.062952Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:39.586573Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:49.107020Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:58.629580Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:32:08.151007Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:32:17.669508Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:32:27.203329Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded | logs_10_102_0_178_MINER-10-102-0-178.txt
10.102.0.179 | 低算力(<50TH/s) | 29.718699 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,3 | 2026-03-29T19:43:55.037413Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-30T03:22:26.626668Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-30T21:51:29.449037Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-31T04:45:11.403241Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-31T05:03:18.319054Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-31T17:09:50.776786Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-31T18:06:57.284904Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-31T20:03:39.400686Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-01T04:43:27.767761Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T07:08:49.790829Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 1725 chips, expected maximum 110 chips on one chain 2026-04-02T14:54:16.132515Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:24:40.303973Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_179_MINER-10-102-0-179.txt
10.102.0.182 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-17T04:04:17.433595Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:05:23.275240Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:06:31.194548Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T06:59:13.741871Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T07:00:25.383078Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T07:40:09.087049Z [ERROR] Tuner error: {ERR:H2} Stage 14: Zero MCR on hashboards [Address(2)] 2026-04-17T08:20:51.000079Z [ERROR] Tuner error: {ERR:H2} Stage 14: Zero MCR on hashboards [Address(2)] 2026-04-17T08:32:17.195190Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T08:33:28.042176Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T09:34:33.890341Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T09:35:41.824411Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T16:07:11.376174Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_182_MINER-10-102-0-182.txt
10.102.0.183 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-20T20:23:23.085528Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T20:24:30.501823Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T20:25:37.924785Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T20:26:46.978020Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T20:37:49.333009Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T20:38:59.682291Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T23:13:29.905780Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T23:14:37.325240Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:40:22.048417Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:41:31.121023Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:42:39.370208Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:43:50.936110Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_183_MINER-10-102-0-183.txt
10.102.0.184 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-19T21:56:43.524426Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:57:52.566642Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T22:58:56.546787Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T23:00:05.612008Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T07:53:16.397196Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T07:54:25.432189Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T14:43:22.738301Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T14:44:30.433976Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T23:13:29.059405Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T23:14:36.472540Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:40:51.180826Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:42:00.240356Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_184_MINER-10-102-0-184.txt
10.102.0.187 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-20T09:39:19.326411Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T10:48:18.705805Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T10:49:26.124804Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T16:58:39.265665Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T16:59:48.318004Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T18:15:06.469006Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T18:16:15.525662Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T18:17:23.792495Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-20T18:18:35.361311Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T18:29:32.789940Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T18:30:45.142525Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T19:31:46.296977Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_187_MINER-10-102-0-187.txt
10.102.0.190 | 无算力(近零<= 2.00TH/s) | 0.301706 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-18T08:53:09.128105Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:54:07.985414Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:17.556950Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T16:26:07.491967Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T16:27:15.413442Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T22:28:14.979987Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T22:29:24.541365Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T04:58:15.354941Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T04:59:24.922778Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T11:02:12.806992Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T12:01:17.249036Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:06.118280Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_190_MINER-10-102-0-190.txt
10.102.0.191 | 低算力(<50TH/s) | 3.439102 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-06T21:29:27.232212Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T08:26:08.872240Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T21:15:41.828549Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:20.537659Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:22:09.947989Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:16:16.281813Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:43.069362Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:59:00.763612Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:49:42.396598Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(3)] 2026-04-12T07:51:08.061955Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:52:09.881748Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T23:22:48.567949Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_191_MINER-10-102-0-191.txt
10.102.0.192 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-19T18:55:54.672568Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:41:48.157164Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:42:57.218305Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:44:05.460215Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:45:17.005674Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:56:15.161423Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:57:24.210758Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T22:58:28.263261Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T22:59:37.310910Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T07:53:12.072522Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T07:54:19.479810Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T07:55:28.527042Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_192_MINER-10-102-0-192.txt
10.102.0.193 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-18T09:54:45.007702Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:07:19.018410Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:08.106546Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-20T17:02:59.304311Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-20T17:06:26.135955Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 509 chips, expected maximum 110 chips on one chain 2026-04-21T01:56:48.553481Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-21T01:58:18.431843Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:42:22.232510Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 841 chips, expected maximum 110 chips on one chain 2026-04-21T02:43:31.297610Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:44:39.394946Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:46:24.953706Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 693 chips, expected maximum 110 chips on one chain 2026-04-21T02:53:44.089343Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 21 (expected: 0x1366 received: 0x1fff) | logs_10_102_0_193_MINER-10-102-0-193.txt
10.102.0.194 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-19T16:10:41.318002Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:03.955334Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:39:13.021532Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:40:21.295438Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:41:32.832488Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:52:30.850912Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:53:39.916313Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T18:54:43.898878Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T18:55:52.954204Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:41:48.107046Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:42:57.170800Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:44:05.434272Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_194_MINER-10-102-0-194.txt
10.102.0.195 | 无算力(0TH/s) | 0.021031 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-18T19:45:29.525208Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-18T20:46:54.302578Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T20:48:02.485673Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:47:35.841442Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:48:58.009823Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T09:50:28.297684Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 5 (expected: 0x1366 received: 0x436) 2026-04-19T09:52:08.403669Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T16:11:04.114318Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T16:13:51.551143Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-19T17:38:19.201292Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:40:48.344350Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-19T17:42:11.709933Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] | logs_10_102_0_195_MINER-10-102-0-195.txt
10.102.0.197 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-22T17:08:10.327471Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:15.471829Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:20.615267Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:25.760951Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:30.902283Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:36.043835Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:41.186425Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:46.331938Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:51.495978Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:56.637318Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:09:01.779875Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:09:06.921286Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_197_MINER-10-102-0-197.txt
10.102.0.198 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-19T17:24:34.577735Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:25:43.659084Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:26:51.701951Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:27:59.316269Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:09.629797Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:39:18.801486Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:40:28.466362Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:41:37.549407Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:52:36.652001Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:53:50.956619Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T18:54:49.704191Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T18:55:57.113900Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_198_MINER-10-102-0-198.txt
10.102.0.199 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-03-31T05:03:09.566253Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-03-31T05:04:20.426710Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-31T18:07:14.766442Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-03-31T18:08:46.412915Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T14:54:02.015133Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-02T14:55:10.179191Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:24:27.294454Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:25:59.524075Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:56:17.084755Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:57:49.735204Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-03T13:56:00.659383Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-03T13:57:12.322987Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_199_MINER-10-102-0-199.txt
10.102.0.202 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-19T01:48:10.218624Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T08:29:03.313115Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T08:30:23.884732Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T12:03:49.408911Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T12:05:24.860162Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T12:06:43.878683Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-19T12:39:08.145266Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-19T12:50:48.481205Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T12:51:57.006612Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T13:53:29.610164Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T13:54:37.480105Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:37:59.922940Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_202_MINER-10-102-0-202.txt
10.102.0.205 | 低算力(<50TH/s) | 41.676614 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:2,3 | 2026-04-22T15:11:24.058342Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:11:30.564105Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:11:37.072677Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:11:43.577876Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:11:50.085339Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:11:56.593062Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:12:03.105270Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:12:09.610332Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:12:16.122453Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:12:22.628942Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:12:29.136034Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:12:35.642405Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) | logs_10_102_0_205_MINER-10-102-0-205.txt
10.102.0.206 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-15T00:15:08.782172Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-15T00:16:25.759131Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:16:25.768710Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-15T00:27:27.869635Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:27:27.883203Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-15T00:28:44.905378Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:28:44.914322Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-15T01:25:04.583018Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-15T01:26:16.276199Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-15T17:45:50.416781Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-15T17:47:17.618679Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-15T18:23:22.966063Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_206_MINER-10-102-0-206.txt
10.102.0.208 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-14T07:32:09.801162Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:32:09.810560Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T07:43:11.304704Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:43:11.313658Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 27 (expected: 0x1366 received: 0x41) 2026-04-14T07:44:26.290338Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:44:26.299249Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-14T08:45:31.090294Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:45:31.099306Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 27 (expected: 0x1366 received: 0x41) 2026-04-14T08:46:44.041226Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:46:44.050220Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 27 (expected: 0x1366 received: 0x41) 2026-04-14T14:47:44.493232Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T14:47:44.502585Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 19 (expected: 0x1366 received: 0x0) | logs_10_102_0_208_MINER-10-102-0-208.txt
10.102.0.209 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-18T07:29:11.962500Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 136 chips, expected maximum 110 chips on one chain 2026-04-18T07:30:19.372471Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T07:31:26.777553Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T07:50:38.058939Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T08:04:28.674092Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T08:10:05.806840Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:16:59.492447Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:18:07.409398Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:15:34.261591Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:16:45.480692Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:30:45.690513Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:33:25.890855Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 838 chips, expected maximum 110 chips on one chain | logs_10_102_0_209_MINER-10-102-0-209.txt
10.102.0.210 | 低算力(<50TH/s) | 4.217342 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-12T07:34:31.946398Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T13:35:31.029014Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T13:36:43.361275Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:08:43.294067Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:10:03.261698Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:07.116027Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:18.307152Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:16:18.122100Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:17:51.299378Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T00:57:27.764230Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T00:58:39.360709Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:07:48.007696Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_210_MINER-10-102-0-210.txt
10.102.0.211 | 低算力(<50TH/s) | 10.593098 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-04T19:19:12.720482Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:17.959985Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:23.200011Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:28.440665Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:33.677445Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:38.920569Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:44.160976Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:49.402023Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:54.640269Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:59.880515Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:20:05.120870Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:20:10.370194Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_211_MINER-10-102-0-211.txt
10.102.0.213 | 低算力(<50TH/s) | 46.250892 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 网络/矿池连接异常；算力板/芯片异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-15T00:27:21.030809Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-15T00:28:32.729934Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-15T18:23:33.510060Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-15T18:25:06.836689Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain ========== errors（错误） ========== 2026-04-15T00:01:37.367505Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-15T00:02:11.414698Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-15T00:02:34.812916Z [ERROR] Failed to resolve ("btc.poolbinance.com", 1800) 2026-04-15T00:02:35.813142Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) 2026-04-15T00:02:35.819325Z [ERROR] Failed to resolve ("bs.poolbinance.com", 3333) 2026-04-15T00:02:56.846657Z [ERROR] Failed to resolve ("btc.poolbinance.com", 1800) 2026-04-15T00:02:57.848943Z [ERROR] Failed to resolve ("bs.poolbinance.com", 3333) | logs_10_102_0_213_MINER-10-102-0-213.txt
10.102.0.214 | 低算力(<50TH/s) | 49.058013 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；电源异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-18T09:54:07.527170Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:18.709904Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:52.157638Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:40:06.421567Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-20T17:06:01.278425Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T17:07:17.253030Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T04:24:59.008724Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T04:26:10.631425Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:21:51.636238Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:24:51.085183Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T18:18:59.707257Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T18:20:11.421903Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_214_MINER-10-102-0-214.txt
10.102.0.215 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-22T19:38:26.731812Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-22T19:39:57.550369Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-23T01:41:30.949296Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-23T01:44:18.784639Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-23T04:43:01.241914Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain ========== errors（错误） ========== 2026-04-22T06:16:19.611954Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) 2026-04-22T06:27:42.511751Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-22T06:29:10.632424Z [ERROR] Failed to resolve ("btc.poolbinance.com", 1800) 2026-04-22T06:29:42.677894Z [ERROR] Failed to resolve ("bs.poolbinance.com", 3333) 2026-04-22T07:16:20.332428Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) 2026-04-22T07:27:43.238637Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) | logs_10_102_0_215_MINER-10-102-0-215.txt
10.102.0.217 | 无算力(0TH/s) | 0.000000 | 单链算力板故障致 SOC 停机（芯片数异常/CRC/通信） | 高 | 矿机服务异常/接口超时；日志中「power off hashboard」为关断算力板动作，勿与 PSU 模块故障混淆 | 日志中「power off hashboard」为关断算力板动作，勿与 PSU 模块故障混淆；矿机服务异常/接口超时 | 根据日志定位异常 Chain（如 find 0 asic、仅 find 部分数量、reg crc error）；断电后重插该链算力板排线与供电，做与正常链互换槽位测试以区分板卡与接口；若故障随板迁移则更换算力板；若固定在槽位则检查控制板与该槽位连线；若固件支持可尝试暂时禁用故障链仅跑健康链（注意功耗与收益） | 2026-04-22 11:04:01 load chain 0 eeprom data 2026-04-22 11:04:02 load chain 1 eeprom data 2026-04-22 11:04:03 load chain 2 eeprom data 2026-04-22 11:04:03 eeprom load ret:0 2026-04-22 11:05:04 Chain 0 only find 0 asic, will power off hash board 0 2026-04-22 11:05:04 ERROR_SOC_INIT: soc init failed! 2026-04-22 11:05:04 stop_mining: soc init failed! 2026-04-22 11:05:04 ****power off hashboard**** "Status": "Alive", "Status": "Alive", [ 0.523574@0] clkmsr ffd18004.meson_clk_msr: failed to get msr ring reg0 [ 0.646548@0] dmi: Firmware registration failed. | logs_10_102_0_217_MINER-10-102-0-217.txt
10.102.0.220 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-18T19:06:58.025593Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:08:09.580340Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:09:18.635463Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:10:29.711674Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:21:28.166110Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:22:35.579846Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T20:23:34.882489Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T20:24:42.291296Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:47:35.912702Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:48:44.972366Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T09:49:49.524355Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T09:50:58.594921Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_220_MINER-10-102-0-220.txt
10.102.0.221 | 无算力(0TH/s) | 0.000000 | 温度传感器通信失败（误报超温/温差保护停机） | 高 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-23T04:55:44.668590Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:46.270340Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:47.862920Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:49.460026Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:51.059440Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:52.658876Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:54.252078Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:55.851449Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:57.451189Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:59.046052Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:56:00.645414Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:56:02.242659Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_221_MINER-10-102-0-221.txt
10.102.1.61 | 无算力(0TH/s) | 0.038302 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-21T12:28:11.822717Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T13:26:17.914464Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:12:32.001675Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:13:43.626380Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:14:46.505599Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-21T15:16:15.902191Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-21T15:27:32.479929Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:28:44.067709Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:20:56.601910Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:32:22.732201Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(3)] 2026-04-21T16:33:53.962857Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:53:41.054032Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] | logs_10_102_1_61_MINER-10-102-1-61.txt
10.102.1.62 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-18T07:39:50.967980Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T08:40:54.955881Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T08:42:03.986790Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:12:26.828194Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:13:35.875249Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:14:44.166205Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:15:55.718547Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:26:53.681863Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:28:50.046861Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:29:59.121125Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:31:07.351894Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:32:18.889232Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_62_MINER-10-102-1-62.txt
10.102.1.63 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；电源异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-17T20:37:50.278465Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T22:51:54.890141Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T22:53:03.951150Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T22:54:18.837853Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T22:55:31.196898Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T23:06:30.264174Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T23:07:41.732919Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T00:08:40.512931Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T00:09:47.934335Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T06:10:47.835267Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T06:11:56.887622Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T07:01:54.122599Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_63_MINER-10-102-1-63.txt
10.102.1.64 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-18T11:44:25.692098Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T12:45:29.681189Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T12:46:38.741468Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T18:47:43.695397Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:45:34.425343Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T01:46:35.411814Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T01:47:45.743068Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T08:28:32.701484Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T08:29:44.259238Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T14:59:15.827261Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T15:00:23.257273Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:05.145576Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_64_MINER-10-102-1-64.txt
10.102.1.65 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-18T11:12:36.230556Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:13:44.501689Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:15:02.282024Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:26:00.295768Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:28:49.778507Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:29:58.838761Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:31:07.106594Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:32:18.607861Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:36:26.072798Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:37:35.123490Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:38:49.105148Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:39:56.530199Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_65_MINER-10-102-1-65.txt
10.102.1.66 | 无算力(近零<= 2.00TH/s) | 0.264167 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-19T13:39:30.474526Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:59:23.290849Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T11:14:13.548352Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:22:04.548833Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T19:45:13.829508Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-22T14:44:43.770770Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 709 chips, expected maximum 110 chips on one chain 2026-04-22T14:49:23.310917Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 196 chips, expected maximum 110 chips on one chain 2026-04-12T07:49:23.282759Z [ERROR] Tuner error: Stage Some(13): restart: Disabled hashboard 3 {HB:3}: {ERR:I2} detected 567 chips, expected maximum 110 chips on one chain 2026-04-13T02:33:04.841753Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1), Address(2), Address(3)] 2026-04-14T03:07:41.442005Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 91 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T03:08:48.328939Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 7 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:01:36.693693Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 91 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing | logs_10_102_1_66_MINER-10-102-1-66.txt
10.102.1.67 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-21T05:07:08.368300Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-21T05:07:08.381203Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-21T05:08:22.740675Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-21T05:08:22.750047Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-21T05:09:36.078042Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-21T05:09:36.091461Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-21T05:20:41.629517Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-21T05:20:41.638891Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-21T05:21:55.181822Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-21T05:21:55.191046Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-21T06:23:02.559626Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-21T06:23:02.568752Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_67_MINER-10-102-1-67.txt
10.102.1.72 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 读取失败（多链初始化失败，SOC 无法启动） | 高 | 矿机服务异常/接口超时；多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 根据 load chain … eeprom / Data load fail / eeprom load ret:-1 定位失败链；逐链重插数据排线与电源，换槽位交叉测试区分板卡与控制板；EEPROM error: CRC … REGION、Fixture data load failed 多为数据损坏或通信问题；多链同时失败优先查共因（排线、控制板 EEPROM 通路、固件版本）；出现 ERROR_SOC_INIT: basic init failed / stop_mining: basic init failed 时，勿先当总线泛化故障；可尝试重刷官方或兼容固件后再测；若单链异常可换板；多链皆失败且排除连接后重点考虑控制板或批量硬件问题 | [ 0.523034@3] clkmsr ffd18004.meson_clk_msr: failed to get msr ring reg0 [ 0.645378@3] dmi: Firmware registration failed. [ 1.517209@2] Initramfs unpacking failed: junk in compressed archive [ 2.012376@3] i2c i2c-1: of_i2c: modalias failure on /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 2.016239@3] i2c i2c-1: Failed to create I2C device for /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 3.155873@3] defendkey: probe of defendkey failed with error -22 [ 3.904145@2] hub 2-0:1.0: config failed, hub doesn't have any ports! (err -19) [ 4.069858@2] thermal thermal_zone0: binding zone soc_thermal with cdev thermal-cpufreq-0 failed:-22 [ 5.690002@1] meson6-dwmac ff3f0000.ethernet eth0: fail to init PTP. 2026-04-22 11:03:53 get test_loop_securely_find_asic_num failed 2026-04-22 11:04:00 fail to write 0:1 2026-04-22 11:04:00 fail to read 0:1 | logs_10_102_1_72_MINER-10-102-1-72.txt
10.102.1.73 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；总线/通信异常；矿机服务异常/接口超时；电源异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-15T00:13:53.843962Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 6 (expected: 0x1366 received: 0x0) 2026-04-15T00:15:14.131569Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:15:14.141783Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 6 (expected: 0x1366 received: 0x0) 2026-04-15T00:16:34.410188Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:16:34.419693Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x0) 2026-04-15T00:27:43.986176Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:27:43.995131Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 7 (expected: 0x1366 received: 0x7f) 2026-04-15T00:29:05.455312Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:29:05.464383Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 6 (expected: 0x1366 received: 0x0) 2026-04-15T02:15:04.772245Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-15T02:16:14.326461Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T06:25:02.321362Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_73_MINER-10-102-1-73.txt
10.102.1.75 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-22T14:52:35.431996Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-22T14:52:35.441297Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-22T15:03:37.369422Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-22T15:03:37.383132Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-22T15:04:54.225454Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-22T15:04:54.236368Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-22T16:05:56.139010Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-22T16:05:56.148507Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-22T16:07:13.158692Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-22T16:07:13.167642Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-22T22:08:16.055249Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-22T22:08:16.064702Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_75_MINER-10-102-1-75.txt
10.102.1.76 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-18T14:43:18.451107Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T14:44:29.997258Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T20:45:28.920625Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T20:46:38.486066Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:47:28.427186Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:48:36.349661Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T09:49:50.921959Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T09:51:13.746451Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 8 (expected: 0x1366 received: 0x0) 2026-04-19T16:09:35.980542Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T16:10:45.523852Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:06.322146Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:39:17.859065Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_76_MINER-10-102-1-76.txt
10.102.1.77 | 无算力(近零<= 2.00TH/s) | 1.803981 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-16T16:24:49.351669Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:24:49.365296Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T16:26:06.214969Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:26:06.224196Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T16:37:09.142676Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:37:09.152012Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T16:38:26.015077Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:38:26.024228Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T17:39:27.925684Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T17:39:27.935268Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T17:40:45.302604Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T17:40:45.311658Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_77_MINER-10-102-1-77.txt

## 无算力
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.176 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-17T22:53:17.719013Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T22:54:38.953415Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T22:56:03.815519Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T23:07:01.243560Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T23:08:20.672504Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T00:09:20.641422Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T00:10:40.643539Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T06:49:00.607621Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T06:50:08.294628Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T07:24:16.205140Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T07:25:25.265135Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T07:26:33.516332Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_176_MINER-10-102-0-176.txt
10.102.0.178 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-20T07:30:42.423669Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:30:51.975216Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:01.501873Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:11.023161Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:20.540639Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:30.062952Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:39.586573Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:49.107020Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:31:58.629580Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:32:08.151007Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:32:17.669508Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-20T07:32:27.203329Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded | logs_10_102_0_178_MINER-10-102-0-178.txt
10.102.0.182 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-17T04:04:17.433595Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:05:23.275240Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:06:31.194548Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T06:59:13.741871Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T07:00:25.383078Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T07:40:09.087049Z [ERROR] Tuner error: {ERR:H2} Stage 14: Zero MCR on hashboards [Address(2)] 2026-04-17T08:20:51.000079Z [ERROR] Tuner error: {ERR:H2} Stage 14: Zero MCR on hashboards [Address(2)] 2026-04-17T08:32:17.195190Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T08:33:28.042176Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T09:34:33.890341Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T09:35:41.824411Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T16:07:11.376174Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_182_MINER-10-102-0-182.txt
10.102.0.183 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-20T20:23:23.085528Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T20:24:30.501823Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T20:25:37.924785Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T20:26:46.978020Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T20:37:49.333009Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T20:38:59.682291Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T23:13:29.905780Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T23:14:37.325240Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:40:22.048417Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:41:31.121023Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:42:39.370208Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:43:50.936110Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_183_MINER-10-102-0-183.txt
10.102.0.184 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-19T21:56:43.524426Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:57:52.566642Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T22:58:56.546787Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T23:00:05.612008Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T07:53:16.397196Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T07:54:25.432189Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T14:43:22.738301Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T14:44:30.433976Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T23:13:29.059405Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T23:14:36.472540Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:40:51.180826Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:42:00.240356Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_184_MINER-10-102-0-184.txt
10.102.0.187 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-20T09:39:19.326411Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T10:48:18.705805Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T10:49:26.124804Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T16:58:39.265665Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T16:59:48.318004Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T18:15:06.469006Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T18:16:15.525662Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T18:17:23.792495Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-20T18:18:35.361311Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T18:29:32.789940Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T18:30:45.142525Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T19:31:46.296977Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_187_MINER-10-102-0-187.txt
10.102.0.190 | 无算力(近零<= 2.00TH/s) | 0.301706 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-18T08:53:09.128105Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:54:07.985414Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:17.556950Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T16:26:07.491967Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T16:27:15.413442Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T22:28:14.979987Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T22:29:24.541365Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T04:58:15.354941Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T04:59:24.922778Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T11:02:12.806992Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T12:01:17.249036Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:06.118280Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_190_MINER-10-102-0-190.txt
10.102.0.192 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-19T18:55:54.672568Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:41:48.157164Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:42:57.218305Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:44:05.460215Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:45:17.005674Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:56:15.161423Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:57:24.210758Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T22:58:28.263261Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T22:59:37.310910Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T07:53:12.072522Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T07:54:19.479810Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T07:55:28.527042Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_192_MINER-10-102-0-192.txt
10.102.0.193 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-18T09:54:45.007702Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:07:19.018410Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:08.106546Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-20T17:02:59.304311Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-20T17:06:26.135955Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 509 chips, expected maximum 110 chips on one chain 2026-04-21T01:56:48.553481Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-21T01:58:18.431843Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:42:22.232510Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 841 chips, expected maximum 110 chips on one chain 2026-04-21T02:43:31.297610Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:44:39.394946Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:46:24.953706Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 693 chips, expected maximum 110 chips on one chain 2026-04-21T02:53:44.089343Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 21 (expected: 0x1366 received: 0x1fff) | logs_10_102_0_193_MINER-10-102-0-193.txt
10.102.0.194 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-19T16:10:41.318002Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:03.955334Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:39:13.021532Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:40:21.295438Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:41:32.832488Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:52:30.850912Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:53:39.916313Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T18:54:43.898878Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T18:55:52.954204Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:41:48.107046Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:42:57.170800Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:44:05.434272Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_194_MINER-10-102-0-194.txt
10.102.0.195 | 无算力(0TH/s) | 0.021031 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-18T19:45:29.525208Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-18T20:46:54.302578Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T20:48:02.485673Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:47:35.841442Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:48:58.009823Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T09:50:28.297684Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 5 (expected: 0x1366 received: 0x436) 2026-04-19T09:52:08.403669Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T16:11:04.114318Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T16:13:51.551143Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-19T17:38:19.201292Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:40:48.344350Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-19T17:42:11.709933Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] | logs_10_102_0_195_MINER-10-102-0-195.txt
10.102.0.197 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-22T17:08:10.327471Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:15.471829Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:20.615267Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:25.760951Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:30.902283Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:36.043835Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:41.186425Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:46.331938Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:51.495978Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:08:56.637318Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:09:01.779875Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-22T17:09:06.921286Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_197_MINER-10-102-0-197.txt
10.102.0.198 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-19T17:24:34.577735Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:25:43.659084Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:26:51.701951Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:27:59.316269Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:09.629797Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:39:18.801486Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:40:28.466362Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:41:37.549407Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:52:36.652001Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:53:50.956619Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T18:54:49.704191Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T18:55:57.113900Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_198_MINER-10-102-0-198.txt
10.102.0.199 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-03-31T05:03:09.566253Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-03-31T05:04:20.426710Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-31T18:07:14.766442Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-03-31T18:08:46.412915Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T14:54:02.015133Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-02T14:55:10.179191Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:24:27.294454Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:25:59.524075Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:56:17.084755Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:57:49.735204Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-03T13:56:00.659383Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-03T13:57:12.322987Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_199_MINER-10-102-0-199.txt
10.102.0.202 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-19T01:48:10.218624Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T08:29:03.313115Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T08:30:23.884732Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T12:03:49.408911Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T12:05:24.860162Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T12:06:43.878683Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-19T12:39:08.145266Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-19T12:50:48.481205Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T12:51:57.006612Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T13:53:29.610164Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T13:54:37.480105Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:37:59.922940Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_202_MINER-10-102-0-202.txt
10.102.0.206 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-15T00:15:08.782172Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-15T00:16:25.759131Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:16:25.768710Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-15T00:27:27.869635Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:27:27.883203Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-15T00:28:44.905378Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:28:44.914322Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-15T01:25:04.583018Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-15T01:26:16.276199Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-15T17:45:50.416781Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-15T17:47:17.618679Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-15T18:23:22.966063Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_206_MINER-10-102-0-206.txt
10.102.0.208 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-14T07:32:09.801162Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:32:09.810560Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-14T07:43:11.304704Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:43:11.313658Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 27 (expected: 0x1366 received: 0x41) 2026-04-14T07:44:26.290338Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T07:44:26.299249Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-14T08:45:31.090294Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:45:31.099306Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 27 (expected: 0x1366 received: 0x41) 2026-04-14T08:46:44.041226Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T08:46:44.050220Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 27 (expected: 0x1366 received: 0x41) 2026-04-14T14:47:44.493232Z [ERROR] {ERR:H1} Hashboard 2 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-14T14:47:44.502585Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 19 (expected: 0x1366 received: 0x0) | logs_10_102_0_208_MINER-10-102-0-208.txt
10.102.0.209 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-18T07:29:11.962500Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 136 chips, expected maximum 110 chips on one chain 2026-04-18T07:30:19.372471Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T07:31:26.777553Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T07:50:38.058939Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T08:04:28.674092Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T08:10:05.806840Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:16:59.492447Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:18:07.409398Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:15:34.261591Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:16:45.480692Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:30:45.690513Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:33:25.890855Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 838 chips, expected maximum 110 chips on one chain | logs_10_102_0_209_MINER-10-102-0-209.txt
10.102.0.215 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-22T19:38:26.731812Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-22T19:39:57.550369Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-23T01:41:30.949296Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-23T01:44:18.784639Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-23T04:43:01.241914Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain ========== errors（错误） ========== 2026-04-22T06:16:19.611954Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) 2026-04-22T06:27:42.511751Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-22T06:29:10.632424Z [ERROR] Failed to resolve ("btc.poolbinance.com", 1800) 2026-04-22T06:29:42.677894Z [ERROR] Failed to resolve ("bs.poolbinance.com", 3333) 2026-04-22T07:16:20.332428Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) 2026-04-22T07:27:43.238637Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) | logs_10_102_0_215_MINER-10-102-0-215.txt
10.102.0.217 | 无算力(0TH/s) | 0.000000 | 单链算力板故障致 SOC 停机（芯片数异常/CRC/通信） | 高 | 矿机服务异常/接口超时；日志中「power off hashboard」为关断算力板动作，勿与 PSU 模块故障混淆 | 日志中「power off hashboard」为关断算力板动作，勿与 PSU 模块故障混淆；矿机服务异常/接口超时 | 根据日志定位异常 Chain（如 find 0 asic、仅 find 部分数量、reg crc error）；断电后重插该链算力板排线与供电，做与正常链互换槽位测试以区分板卡与接口；若故障随板迁移则更换算力板；若固定在槽位则检查控制板与该槽位连线；若固件支持可尝试暂时禁用故障链仅跑健康链（注意功耗与收益） | 2026-04-22 11:04:01 load chain 0 eeprom data 2026-04-22 11:04:02 load chain 1 eeprom data 2026-04-22 11:04:03 load chain 2 eeprom data 2026-04-22 11:04:03 eeprom load ret:0 2026-04-22 11:05:04 Chain 0 only find 0 asic, will power off hash board 0 2026-04-22 11:05:04 ERROR_SOC_INIT: soc init failed! 2026-04-22 11:05:04 stop_mining: soc init failed! 2026-04-22 11:05:04 ****power off hashboard**** "Status": "Alive", "Status": "Alive", [ 0.523574@0] clkmsr ffd18004.meson_clk_msr: failed to get msr ring reg0 [ 0.646548@0] dmi: Firmware registration failed. | logs_10_102_0_217_MINER-10-102-0-217.txt
10.102.0.220 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-18T19:06:58.025593Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:08:09.580340Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:09:18.635463Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:10:29.711674Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:21:28.166110Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:22:35.579846Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T20:23:34.882489Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T20:24:42.291296Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:47:35.912702Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:48:44.972366Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T09:49:49.524355Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T09:50:58.594921Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_220_MINER-10-102-0-220.txt
10.102.0.221 | 无算力(0TH/s) | 0.000000 | 温度传感器通信失败（误报超温/温差保护停机） | 高 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-23T04:55:44.668590Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:46.270340Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:47.862920Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:49.460026Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:51.059440Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:52.658876Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:54.252078Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:55.851449Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:57.451189Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:55:59.046052Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:56:00.645414Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:56:02.242659Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_221_MINER-10-102-0-221.txt
10.102.1.61 | 无算力(0TH/s) | 0.038302 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-21T12:28:11.822717Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T13:26:17.914464Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:12:32.001675Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:13:43.626380Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:14:46.505599Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-21T15:16:15.902191Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-21T15:27:32.479929Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:28:44.067709Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:20:56.601910Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:32:22.732201Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(3)] 2026-04-21T16:33:53.962857Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:53:41.054032Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] | logs_10_102_1_61_MINER-10-102-1-61.txt
10.102.1.62 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-18T07:39:50.967980Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T08:40:54.955881Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T08:42:03.986790Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:12:26.828194Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:13:35.875249Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:14:44.166205Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:15:55.718547Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:26:53.681863Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:28:50.046861Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:29:59.121125Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:31:07.351894Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:32:18.889232Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_62_MINER-10-102-1-62.txt
10.102.1.63 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；电源异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-17T20:37:50.278465Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T22:51:54.890141Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T22:53:03.951150Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T22:54:18.837853Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T22:55:31.196898Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T23:06:30.264174Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T23:07:41.732919Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T00:08:40.512931Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T00:09:47.934335Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T06:10:47.835267Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T06:11:56.887622Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T07:01:54.122599Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_63_MINER-10-102-1-63.txt
10.102.1.64 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-18T11:44:25.692098Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T12:45:29.681189Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T12:46:38.741468Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T18:47:43.695397Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T19:45:34.425343Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T01:46:35.411814Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T01:47:45.743068Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T08:28:32.701484Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T08:29:44.259238Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T14:59:15.827261Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T15:00:23.257273Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:05.145576Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_64_MINER-10-102-1-64.txt
10.102.1.65 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-18T11:12:36.230556Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:13:44.501689Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:15:02.282024Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:26:00.295768Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:28:49.778507Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:29:58.838761Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:31:07.106594Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:32:18.607861Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:36:26.072798Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:37:35.123490Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:38:49.105148Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T11:39:56.530199Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_65_MINER-10-102-1-65.txt
10.102.1.66 | 无算力(近零<= 2.00TH/s) | 0.264167 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-19T13:39:30.474526Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T21:59:23.290849Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T11:14:13.548352Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:22:04.548833Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T19:45:13.829508Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-22T14:44:43.770770Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 709 chips, expected maximum 110 chips on one chain 2026-04-22T14:49:23.310917Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 196 chips, expected maximum 110 chips on one chain 2026-04-12T07:49:23.282759Z [ERROR] Tuner error: Stage Some(13): restart: Disabled hashboard 3 {HB:3}: {ERR:I2} detected 567 chips, expected maximum 110 chips on one chain 2026-04-13T02:33:04.841753Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1), Address(2), Address(3)] 2026-04-14T03:07:41.442005Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 91 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T03:08:48.328939Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 7 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:01:36.693693Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 91 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing | logs_10_102_1_66_MINER-10-102-1-66.txt
10.102.1.67 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-21T05:07:08.368300Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-21T05:07:08.381203Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-21T05:08:22.740675Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-21T05:08:22.750047Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-21T05:09:36.078042Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-21T05:09:36.091461Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-21T05:20:41.629517Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-21T05:20:41.638891Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-21T05:21:55.181822Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-21T05:21:55.191046Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-21T06:23:02.559626Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-21T06:23:02.568752Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_67_MINER-10-102-1-67.txt
10.102.1.72 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 读取失败（多链初始化失败，SOC 无法启动） | 高 | 矿机服务异常/接口超时；多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 根据 load chain … eeprom / Data load fail / eeprom load ret:-1 定位失败链；逐链重插数据排线与电源，换槽位交叉测试区分板卡与控制板；EEPROM error: CRC … REGION、Fixture data load failed 多为数据损坏或通信问题；多链同时失败优先查共因（排线、控制板 EEPROM 通路、固件版本）；出现 ERROR_SOC_INIT: basic init failed / stop_mining: basic init failed 时，勿先当总线泛化故障；可尝试重刷官方或兼容固件后再测；若单链异常可换板；多链皆失败且排除连接后重点考虑控制板或批量硬件问题 | [ 0.523034@3] clkmsr ffd18004.meson_clk_msr: failed to get msr ring reg0 [ 0.645378@3] dmi: Firmware registration failed. [ 1.517209@2] Initramfs unpacking failed: junk in compressed archive [ 2.012376@3] i2c i2c-1: of_i2c: modalias failure on /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 2.016239@3] i2c i2c-1: Failed to create I2C device for /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 3.155873@3] defendkey: probe of defendkey failed with error -22 [ 3.904145@2] hub 2-0:1.0: config failed, hub doesn't have any ports! (err -19) [ 4.069858@2] thermal thermal_zone0: binding zone soc_thermal with cdev thermal-cpufreq-0 failed:-22 [ 5.690002@1] meson6-dwmac ff3f0000.ethernet eth0: fail to init PTP. 2026-04-22 11:03:53 get test_loop_securely_find_asic_num failed 2026-04-22 11:04:00 fail to write 0:1 2026-04-22 11:04:00 fail to read 0:1 | logs_10_102_1_72_MINER-10-102-1-72.txt
10.102.1.73 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；总线/通信异常；矿机服务异常/接口超时；电源异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-15T00:13:53.843962Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 6 (expected: 0x1366 received: 0x0) 2026-04-15T00:15:14.131569Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:15:14.141783Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 6 (expected: 0x1366 received: 0x0) 2026-04-15T00:16:34.410188Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:16:34.419693Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x0) 2026-04-15T00:27:43.986176Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:27:43.995131Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 7 (expected: 0x1366 received: 0x7f) 2026-04-15T00:29:05.455312Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-15T00:29:05.464383Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 6 (expected: 0x1366 received: 0x0) 2026-04-15T02:15:04.772245Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-15T02:16:14.326461Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T06:25:02.321362Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_73_MINER-10-102-1-73.txt
10.102.1.75 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-22T14:52:35.431996Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-22T14:52:35.441297Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-22T15:03:37.369422Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-22T15:03:37.383132Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-22T15:04:54.225454Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-22T15:04:54.236368Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-22T16:05:56.139010Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-22T16:05:56.148507Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-22T16:07:13.158692Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-22T16:07:13.167642Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-22T22:08:16.055249Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-22T22:08:16.064702Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_75_MINER-10-102-1-75.txt
10.102.1.76 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-18T14:43:18.451107Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T14:44:29.997258Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T20:45:28.920625Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T20:46:38.486066Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:47:28.427186Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:48:36.349661Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T09:49:50.921959Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T09:51:13.746451Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 8 (expected: 0x1366 received: 0x0) 2026-04-19T16:09:35.980542Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T16:10:45.523852Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:06.322146Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:39:17.859065Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_76_MINER-10-102-1-76.txt
10.102.1.77 | 无算力(近零<= 2.00TH/s) | 1.803981 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-16T16:24:49.351669Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:24:49.365296Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T16:26:06.214969Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:26:06.224196Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T16:37:09.142676Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:37:09.152012Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T16:38:26.015077Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:38:26.024228Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T17:39:27.925684Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T17:39:27.935268Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T17:40:45.302604Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T17:40:45.311658Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_77_MINER-10-102-1-77.txt

## 低算力
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.162 | 低算力(<50TH/s) | 46.767700 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-23T04:54:25.607447Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:27.200295Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:28.802620Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:30.395338Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:31.997449Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:33.592581Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:35.190051Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:36.787748Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:38.383080Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:39.985431Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:41.580488Z [WARN] Temperature Sensor Read Failed 2026-04-23T04:54:43.178102Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_162_MINER-10-102-0-162.txt
10.102.0.174 | 低算力(<50TH/s) | 36.487960 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-03-29T19:43:50.469907Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-03-30T03:22:33.181202Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-03-31T18:07:16.144838Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-03-31T18:18:41.776610Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-02T05:33:24.183273Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T05:34:33.408224Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:24:43.433314Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:54:29.884466Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-02T17:17:21.178485Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-02T18:41:31.390484Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-02T19:44:31.798110Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-03T07:02:00.401209Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_174_MINER-10-102-0-174.txt
10.102.0.179 | 低算力(<50TH/s) | 29.718699 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,3 | 2026-03-29T19:43:55.037413Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-30T03:22:26.626668Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-30T21:51:29.449037Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-31T04:45:11.403241Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-31T05:03:18.319054Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-31T17:09:50.776786Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-31T18:06:57.284904Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-03-31T20:03:39.400686Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-01T04:43:27.767761Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T07:08:49.790829Z [ERROR] Tuner error: Stage Some(8): restart: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 1725 chips, expected maximum 110 chips on one chain 2026-04-02T14:54:16.132515Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-02T16:24:40.303973Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_179_MINER-10-102-0-179.txt
10.102.0.191 | 低算力(<50TH/s) | 3.439102 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-06T21:29:27.232212Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T08:26:08.872240Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T21:15:41.828549Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:20.537659Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:22:09.947989Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:16:16.281813Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:43.069362Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:59:00.763612Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:49:42.396598Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(3)] 2026-04-12T07:51:08.061955Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:52:09.881748Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-12T23:22:48.567949Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_191_MINER-10-102-0-191.txt
10.102.0.205 | 低算力(<50TH/s) | 41.676614 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:2,3 | 2026-04-22T15:11:24.058342Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:11:30.564105Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:11:37.072677Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:11:43.577876Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:11:50.085339Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:11:56.593062Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:12:03.105270Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:12:09.610332Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:12:16.122453Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:12:22.628942Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:12:29.136034Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) 2026-04-22T15:12:35.642405Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 3: No such device or address (os error 6) | logs_10_102_0_205_MINER-10-102-0-205.txt
10.102.0.210 | 低算力(<50TH/s) | 4.217342 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-12T07:34:31.946398Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T13:35:31.029014Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T13:36:43.361275Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:08:43.294067Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T00:10:03.261698Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:07.116027Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:18.307152Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:16:18.122100Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:17:51.299378Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T00:57:27.764230Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-14T00:58:39.360709Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-14T03:07:48.007696Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_210_MINER-10-102-0-210.txt
10.102.0.211 | 低算力(<50TH/s) | 10.593098 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-04T19:19:12.720482Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:17.959985Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:23.200011Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:28.440665Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:33.677445Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:38.920569Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:44.160976Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:49.402023Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:54.640269Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:19:59.880515Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:20:05.120870Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-04T19:20:10.370194Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_211_MINER-10-102-0-211.txt
10.102.0.213 | 低算力(<50TH/s) | 46.250892 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 网络/矿池连接异常；算力板/芯片异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-15T00:27:21.030809Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-15T00:28:32.729934Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-15T18:23:33.510060Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-15T18:25:06.836689Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain ========== errors（错误） ========== 2026-04-15T00:01:37.367505Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-15T00:02:11.414698Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2026-04-15T00:02:34.812916Z [ERROR] Failed to resolve ("btc.poolbinance.com", 1800) 2026-04-15T00:02:35.813142Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) 2026-04-15T00:02:35.819325Z [ERROR] Failed to resolve ("bs.poolbinance.com", 3333) 2026-04-15T00:02:56.846657Z [ERROR] Failed to resolve ("btc.poolbinance.com", 1800) 2026-04-15T00:02:57.848943Z [ERROR] Failed to resolve ("bs.poolbinance.com", 3333) | logs_10_102_0_213_MINER-10-102-0-213.txt
10.102.0.214 | 低算力(<50TH/s) | 49.058013 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；电源异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-18T09:54:07.527170Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:18.709904Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:38:52.157638Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:40:06.421567Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-20T17:06:01.278425Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-20T17:07:17.253030Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T04:24:59.008724Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T04:26:10.631425Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:21:51.636238Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:24:51.085183Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T18:18:59.707257Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T18:20:11.421903Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_214_MINER-10-102-0-214.txt