## 全部异常
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.150 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 总线/通信异常；算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,3 | 2026-04-24T18:45:25.185110Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 550 chips, expected maximum 110 chips on one chain 2026-04-24T18:47:37.406915Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:53:44.892479Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(2)] 2026-04-24T18:56:09.372264Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T19:09:15.127351Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T19:13:41.057030Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 383 chips, expected maximum 110 chips on one chain ========== errors（错误） ========== 2015-01-01T00:00:39.276118Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) 2015-01-01T00:00:39.294576Z [ERROR] Failed to resolve ("btc.poolbinance.com", 1800) 2015-01-01T00:00:59.302343Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2015-01-01T00:00:59.517275Z [ERROR] Sensor hb2.73 probing failed: Setting pointer register to 0x07 for I2c read of 1 bytes: No such device or address (os error 6) 2015-01-01T00:00:59.555254Z [ERROR] Sensor hb3.74 probing failed: Setting pointer register to 0x07 for I2c read of 1 bytes: No such device or address (os error 6) | logs_10_102_0_150_MINER-10-102-0-150.txt
10.102.0.151 | 无算力(近零<= 2.00TH/s) | 0.090040 | 算力板部分失效（芯片数量严重不足） | 高 | 算力板/芯片异常；网络/矿池连接异常 | 算力板/芯片异常；网络/矿池连接异常 | 定位异常算力板并单板测试；检查该板排线、供电及散热状态；复位或升级固件后复测芯片识别数量；若芯片长期缺失，安排维修或更换算力板；当前日志涉及 HB:1 |  | logs_10_102_0_151_MINER-10-102-0-151.txt
10.102.0.155 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-27T02:45:49.720743Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T02:45:49.729842Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T02:47:17.588359Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T02:47:17.597507Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T02:48:51.568768Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T02:48:51.577822Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T02:50:26.740918Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T02:50:26.750226Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T02:56:44.467952Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T02:56:44.477887Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T02:57:54.689569Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T02:57:54.702605Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_155_MINER-10-102-0-155.txt
10.102.0.156 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,3 |  | logs_10_102_0_156_MINER-10-102-0-156.txt
10.102.0.157 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-26T21:08:35.079058Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:10:53.305623Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 13 (expected: 0x1366 received: 0x3) 2026-04-26T21:22:00.902846Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 13 (expected: 0x1366 received: 0x7f) 2026-04-26T21:24:13.325100Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:34:46.206240Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 16 (expected: 0x1366 received: 0x20) 2026-04-26T21:36:09.896950Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:38:28.631521Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:40:20.582686Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 16 (expected: 0x1366 received: 0x1004) 2026-04-26T21:51:31.897556Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 13 (expected: 0x1366 received: 0xe03) 2026-04-26T21:52:58.825350Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T22:47:43.703226Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 13 (expected: 0x1366 received: 0x0) 2026-04-26T22:49:16.349931Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_157_MINER-10-102-0-157.txt
10.102.0.158 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 网络/矿池连接异常；算力板/芯片异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 |  | logs_10_102_0_158_MINER-10-102-0-158.txt
10.102.0.162 | 低算力(<50TH/s) | 39.050030 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-28T12:57:17.556941Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:19.154312Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:20.747039Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:22.344673Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:23.946166Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:25.541377Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:27.138960Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:28.736411Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:30.339119Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:31.934235Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:33.531794Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:35.129274Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_162_MINER-10-102-0-162.txt
10.102.0.174 | 低算力(<50TH/s) | 36.779636 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-07T21:10:08.476864Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T21:15:16.995517Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:18.878485Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:06:02.077325Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:20:36.462137Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:16:12.772087Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:36.726948Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:33:21.335733Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:30.532566Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:36:12.111990Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-12T07:38:31.749507Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-12T08:46:39.169679Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_174_MINER-10-102-0-174.txt
10.102.0.176 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-24T19:55:28.846082Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T19:56:52.548670Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T20:59:27.157328Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:00:47.793588Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:02:57.179757Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:04:22.015704Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:15:33.584417Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:17:02.641700Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T22:18:12.868505Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T22:19:33.265558Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-25T12:11:13.128633Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-25T12:12:20.545010Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_176_MINER-10-102-0-176.txt
10.102.0.178 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-27T03:48:03.004348Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:49:14.066981Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:49:14.080605Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:50:30.928781Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:50:30.937916Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:55:36.485470Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:55:36.494631Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:57:36.545757Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:57:36.555342Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:58:50.566708Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:58:50.575987Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T04:00:05.334328Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_0_178_MINER-10-102-0-178.txt
10.102.0.179 | 低算力(<50TH/s) | 46.571303 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,3 | 2026-04-10T23:16:34.685589Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:18:19.532950Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T12:10:21.954887Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T12:11:30.907960Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:05.253515Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-12T07:37:57.811006Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-12T23:23:00.354405Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:24:19.565920Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:06.426416Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:15.979449Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:16:23.328355Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-04-13T19:17:44.536601Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_179_MINER-10-102-0-179.txt
10.102.0.182 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-27T01:08:06.828046Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:09:27.304339Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:50:27.174912Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:51:36.243437Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:53:04.534778Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:54:31.275912Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:05:31.989442Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:06:40.688727Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:13:49.677526Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:14:58.734854Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:16:06.968971Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:17:33.295446Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_182_MINER-10-102-0-182.txt
10.102.0.183 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T20:23:07.795022Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:25:28.502290Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:26:49.004945Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:36:36.065160Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:38:06.435571Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:39:26.866391Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:41:48.345368Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:52:58.471689Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:54:17.616898Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:57:05.204370Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:59:12.307797Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:00:31.882966Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_183_MINER-10-102-0-183.txt
10.102.0.184 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T21:51:54.399776Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:48:12.685709Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:49:33.299363Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:50:57.005296Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:52:23.338739Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:03:34.540893Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:05:03.554082Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:50:49.233591Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:52:09.860077Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:53:38.856977Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:54:58.876194Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T00:06:08.169319Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_184_MINER-10-102-0-184.txt
10.102.0.187 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-27T06:03:47.131218Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:03:50.912796Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:03:54.695924Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:03:58.481592Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:02.264388Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:06.046984Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:09.829839Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:13.615074Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:17.396650Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:21.178424Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:24.961794Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:28.743880Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) | logs_10_102_0_187_MINER-10-102-0-187.txt
10.102.0.190 | 无算力(近零<= 2.00TH/s) | 0.164411 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-24T15:11:51.063364Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:13:03.576947Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:14:20.741568Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T15:15:40.854094Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T15:18:13.781429Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:19:34.232196Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:20:40.740036Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T15:21:59.792715Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T15:33:13.858563Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:34:27.682169Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:41:39.716949Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:44:18.854463Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_190_MINER-10-102-0-190.txt
10.102.0.191 | 无算力(近零<= 2.00TH/s) | 1.316238 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-15T23:44:42.360430Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T14:12:02.961961Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T14:13:43.041980Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 11 (expected: 0x1366 received: 0xd00) 2026-04-16T19:29:31.053982Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T22:57:49.241626Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:55:08.309141Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:57:26.595112Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:41:46.729661Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain ========== errors（错误） ========== 2015-01-01T00:00:39.436262Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) 2015-01-01T00:00:59.456349Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2015-01-01T00:01:08.891236Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) | logs_10_102_0_191_MINER-10-102-0-191.txt
10.102.0.192 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T21:34:45.235844Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:36:08.932820Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:37:29.640569Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:38:55.925427Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:50:06.372967Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:51:27.036423Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:47:43.794770Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:49:04.405283Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:50:25.040725Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:51:46.199483Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:02:57.118249Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:04:18.921479Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_192_MINER-10-102-0-192.txt
10.102.0.193 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-27T01:51:37.173079Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:52:52.168615Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:54:11.202688Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:05:12.088183Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:06:19.803406Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:13:49.599211Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:14:58.657972Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:16:06.908631Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:17:18.514875Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:21:25.870816Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:22:34.931067Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:23:43.220573Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_193_MINER-10-102-0-193.txt
10.102.0.194 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-27T02:19:33.728213Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T02:21:26.866662Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:22:35.930584Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:23:49.855230Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:25:10.379262Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:36:09.581650Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:37:16.995135Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:40:17.745914Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T02:40:27.262816Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T02:40:36.788445Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T02:40:46.306236Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T02:42:07.756431Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_194_MINER-10-102-0-194.txt
10.102.0.195 | 无算力(0TH/s) | 0.001248 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-27T19:22:07.981848Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:11.761223Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:15.539777Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:19.316390Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:23.094066Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:26.872426Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:30.650158Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:34.427743Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:38.206302Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:41.983237Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:45.762293Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:49.539896Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) | logs_10_102_0_195_MINER-10-102-0-195.txt
10.102.0.197 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-27T13:03:28.744477Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:03:33.886190Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:03:39.031117Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:03:44.172706Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:03:49.313991Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:03:54.457426Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:03:59.597346Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:04:04.764712Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:04:09.908898Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:04:15.052396Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:04:20.193766Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:04:25.337452Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_197_MINER-10-102-0-197.txt
10.102.0.198 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2 | 2026-04-26T19:07:08.234538Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T19:09:01.767539Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-26T19:11:32.599630Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-26T19:22:58.868385Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T19:25:32.859372Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T19:42:53.964887Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T19:46:52.235074Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T19:49:19.685201Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T19:51:32.722732Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-26T19:54:23.477030Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-26T20:05:47.962514Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:08:14.628183Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_198_MINER-10-102-0-198.txt
10.102.0.199 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T19:52:04.473850Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:03:15.788975Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:04:49.091827Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:11:19.623849Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:12:52.235346Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:14:21.977926Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:15:53.913548Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:21:42.879143Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:23:15.533618Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:24:45.254035Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:26:12.388668Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:36:52.135969Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_199_MINER-10-102-0-199.txt
10.102.0.202 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-24T18:02:28.278721Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:14:28.463380Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:16:16.272537Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:37:29.071435Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:39:29.139989Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:00:07.124030Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:22:13.914159Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:24:20.495585Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:28:33.695546Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(3)] 2026-04-26T20:35:20.170651Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-26T20:47:16.386278Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:48:40.815600Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_202_MINER-10-102-0-202.txt
10.102.0.206 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-25T12:09:36.407445Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-25T12:10:45.978957Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-25T12:12:36.282164Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-25T12:15:06.814754Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-25T12:26:28.356370Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-25T12:27:39.201000Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-25T13:28:51.269749Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-25T13:30:05.432111Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-25T19:31:15.162183Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-25T19:32:42.891122Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-25T19:53:53.212743Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-25T19:55:26.338239Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_206_MINER-10-102-0-206.txt
10.102.0.208 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-20T07:53:46.847864Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I2} detected 437 chips, expected maximum 110 chips on one chain 2026-04-20T17:03:10.260051Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-21T02:40:56.528781Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:53:44.204086Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T04:24:45.860536Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:13:02.600034Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:21:36.405075Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T18:18:30.025302Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-22T02:15:37.786314Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-22T11:05:47.035661Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-22T14:49:23.279039Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T06:49:04.228294Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 23 (expected: 0x1366 received: 0xd47) | logs_10_102_0_208_MINER-10-102-0-208.txt
10.102.0.209 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 总线/通信异常；算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-22T14:48:51.791483Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-22T15:28:13.698439Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 494 chips, expected maximum 110 chips on one chain 2026-04-22T15:29:21.117328Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-22T15:37:15.770564Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 503 chips, expected maximum 110 chips on one chain 2026-04-22T20:51:32.386809Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-23T00:21:58.360707Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-23T01:29:54.097606Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 117 chips, expected maximum 110 chips on one chain 2026-04-23T01:31:39.820170Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-23T02:36:09.342880Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-23T02:45:33.596010Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 550 chips, expected maximum 110 chips on one chain 2026-04-23T04:53:37.711934Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 215 chips, expected maximum 110 chips on one chain 2026-04-23T04:54:57.534288Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_209_MINER-10-102-0-209.txt
10.102.0.210 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:2,3 | 2026-04-15T23:44:05.584004Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-15T23:45:24.870014Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T14:12:07.658118Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T14:13:14.582528Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T19:22:06.303979Z [ERROR] Tuner error: Stage 4: Stage 4: Zero MCR on hashboards [Address(1)] 2026-04-16T19:27:09.319707Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T19:28:30.536220Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:55:08.526754Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:56:33.551728Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:57:27.016490Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:58:38.229884Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:54:08.750536Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_210_MINER-10-102-0-210.txt
10.102.0.211 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-19T17:39:31.326342Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 1284 chips, expected maximum 110 chips on one chain 2026-04-21T12:37:18.811036Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1), Address(2), Address(3)] 2026-04-21T12:57:38.325966Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(1), Address(2), Address(3)] 2026-04-21T13:18:38.706221Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2), Address(3)] 2026-04-21T13:37:50.806157Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2), Address(3)] 2026-04-21T14:06:30.611478Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2), Address(3)] 2026-04-21T14:07:55.733509Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:08:58.428932Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:12:54.269367Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:31:48.468257Z [ERROR] Tuner error: Stage Some(13): restart: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:06:28.750036Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-21T16:35:34.662059Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 3 (expected: 0x1366 received: 0x16ff) | logs_10_102_0_211_MINER-10-102-0-211.txt
10.102.0.213 | 低算力(<50TH/s) | 46.409840 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 网络/矿池连接异常；算力板/芯片异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-15T23:42:54.112824Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-15T23:44:36.223520Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T14:12:32.171279Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-16T14:13:45.428336Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T19:29:13.137255Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-16T19:30:38.371121Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:55:07.436139Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:56:34.691817Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:57:18.820070Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:58:28.392112Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:54:08.697631Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:18.271886Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_213_MINER-10-102-0-213.txt
10.102.0.215 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-26T21:04:00.091437Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:05:29.444169Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-26T21:06:50.935007Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:08:17.979733Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:19:32.558110Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:20:54.427683Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-26T21:34:46.622319Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:36:07.256417Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-26T21:37:28.664390Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:38:55.141443Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:50:04.847389Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:51:25.349495Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) | logs_10_102_0_215_MINER-10-102-0-215.txt
10.102.0.216 | 低算力(<50TH/s) | 40.328792 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:2,3 | 2026-04-26T07:38:19.305455Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:24.559131Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:29.813314Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:35.069519Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:40.323413Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:45.575877Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:50.829303Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:56.088056Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:39:01.342124Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:39:06.595887Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:39:11.852336Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:39:17.106776Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_216_MINER-10-102-0-216.txt
10.102.0.217 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-27T13:24:54.139496Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:24:59.282076Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:04.458640Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:09.603903Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:14.746708Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:19.891783Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:25.036873Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:30.181174Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:35.325947Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:40.469070Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:45.645235Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:50.786745Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_217_MINER-10-102-0-217.txt
10.102.0.218 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-27T03:10:48.296852Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:10:52.183952Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:10:56.071024Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:10:59.960516Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:03.848595Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:07.735420Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:11.623146Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:15.511187Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:19.398661Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:23.288223Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:27.174647Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:31.062555Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) | logs_10_102_0_218_MINER-10-102-0-218.txt
10.102.0.220 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-24T15:44:22.267446Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:46:31.792257Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:51:32.788042Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-04-24T15:52:51.448308Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:54:07.341873Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T16:05:39.810283Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T16:12:41.644173Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T17:10:06.541877Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x0) 2026-04-24T17:11:33.242512Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T17:13:40.491776Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T17:25:05.538390Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T17:50:25.044038Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_220_MINER-10-102-0-220.txt
10.102.0.223 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 读取失败（多链初始化失败，SOC 无法启动） | 高 | 矿机服务异常/接口超时；多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 根据 load chain … eeprom / Data load fail / eeprom load ret:-1 定位失败链；逐链重插数据排线与电源，换槽位交叉测试区分板卡与控制板；EEPROM error: CRC … REGION、Fixture data load failed 多为数据损坏或通信问题；多链同时失败优先查共因（排线、控制板 EEPROM 通路、固件版本）；出现 ERROR_SOC_INIT: basic init failed / stop_mining: basic init failed 时，勿先当总线泛化故障；可尝试重刷官方或兼容固件后再测；若单链异常可换板；多链皆失败且排除连接后重点考虑控制板或批量硬件问题 | [ 0.527257@0] clkmsr ffd18004.meson_clk_msr: failed to get msr ring reg0 [ 0.646373@0] dmi: Firmware registration failed. [ 1.518589@0] Initramfs unpacking failed: junk in compressed archive [ 2.021667@3] i2c i2c-1: of_i2c: modalias failure on /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 2.025474@3] i2c i2c-1: Failed to create I2C device for /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 3.185931@0] defendkey: probe of defendkey failed with error -22 [ 3.934175@1] hub 2-0:1.0: config failed, hub doesn't have any ports! (err -19) [ 4.099850@1] thermal thermal_zone0: binding zone soc_thermal with cdev thermal-cpufreq-0 failed:-22 [ 5.767015@0] meson6-dwmac ff3f0000.ethernet eth0: fail to init PTP. 2026-04-27 08:25:12 get test_loop_securely_find_asic_num failed 2026-04-27 08:25:18 fail to write 0:1 2026-04-27 08:25:18 fail to read 0:1 | logs_10_102_0_223_MINER-10-102-0-223.txt
10.102.1.61 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-27T04:21:52.234303Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:01.746706Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:11.266750Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:20.782708Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:30.300567Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:39.816752Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:49.330389Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:58.850620Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:23:08.370482Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:23:17.886800Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:23:27.413465Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:23:36.947975Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded | logs_10_102_1_61_MINER-10-102-1-61.txt
10.102.1.62 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T20:03:57.462748Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:05:40.808932Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:10:59.555607Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:12:40.098440Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:14:33.926242Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:16:23.290195Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:21:38.757638Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:23:21.157215Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:25:11.412288Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:26:56.124564Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:36:36.032624Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:38:25.429258Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_62_MINER-10-102-1-62.txt
10.102.1.63 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T21:36:06.727145Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:37:36.743836Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:38:58.331714Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:50:05.863126Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:51:25.496948Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:47:43.767537Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:49:05.414763Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:50:34.780054Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:52:02.220171Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:03:13.723531Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:04:35.341568Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:50:19.980077Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_63_MINER-10-102-1-63.txt
10.102.1.64 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-24T07:33:43.700982Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T07:44:44.427934Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T07:45:53.750141Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T08:46:51.180063Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T08:48:00.232658Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T13:27:07.344951Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T13:28:16.400416Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T13:29:36.682072Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T13:31:15.573848Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T13:42:21.015997Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x1040) 2026-04-24T13:43:34.437274Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:32:35.639838Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 122 chips, expected maximum 110 chips on one chain | logs_10_102_1_64_MINER-10-102-1-64.txt
10.102.1.65 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T22:49:06.086522Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:52:17.808717Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:53:41.211642Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:04:50.378187Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:07:39.507018Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:50:21.030849Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:53:24.812105Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:54:51.110347Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:57:51.714423Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T00:09:01.448307Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T00:11:55.036838Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:12:53.741160Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_65_MINER-10-102-1-65.txt
10.102.1.66 | 无算力(近零<= 2.00TH/s) | 0.227468 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-12T07:49:23.282759Z [ERROR] Tuner error: Stage Some(13): restart: Disabled hashboard 3 {HB:3}: {ERR:I2} detected 567 chips, expected maximum 110 chips on one chain 2026-04-13T02:33:04.841753Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1), Address(2), Address(3)] 2026-04-14T03:07:41.442005Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 91 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T03:08:48.328939Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 7 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:01:36.693693Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 91 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:02:45.327352Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 7 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:04:05.207852Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 109 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:05:45.133862Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 91 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:16:42.023726Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 91 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:17:48.909650Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 7 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing ========== errors（错误） ========== 2026-04-05T21:46:38.116882Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) | logs_10_102_1_66_MINER-10-102-1-66.txt
10.102.1.67 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-27T03:14:21.577947Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:17:39.620258Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:17:39.629413Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:18:55.629569Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:18:55.638943Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:20:09.977174Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:20:09.990002Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:21:26.981116Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:21:26.990196Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:33:08.397509Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:33:08.406789Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:34:24.406479Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_1_67_MINER-10-102-1-67.txt
10.102.1.72 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-27T03:12:38.643271Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:12:38.652289Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:15:21.303153Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:15:21.312375Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:16:31.647452Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:16:31.658734Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:17:45.466847Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:17:45.476973Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:19:02.723045Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:19:02.732397Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:30:05.815573Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:30:05.825122Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_72_MINER-10-102-1-72.txt
10.102.1.73 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-24T18:40:22.356784Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T19:51:47.622361Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-24T20:17:35.803245Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T20:19:44.259293Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:41:37.359696Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:43:10.804105Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:50:19.174522Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:52:23.406443Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T22:34:57.843080Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-24T23:34:23.390659Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T23:36:25.783262Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-25T12:14:48.341029Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(1)] | logs_10_102_1_73_MINER-10-102-1-73.txt
10.102.1.75 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-27T03:48:57.582458Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:51:21.521755Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:51:21.528590Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:52:35.614986Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:52:35.621489Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:53:46.847633Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:53:46.854145Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:55:26.538187Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:55:26.545283Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:57:26.597949Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:57:26.604673Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:58:40.769354Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_1_75_MINER-10-102-1-75.txt
10.102.1.76 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T20:13:38.766514Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:15:02.489832Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:21:38.790891Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:23:01.508529Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:24:20.586133Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:25:49.812890Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:35:37.414460Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:36:59.304094Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:38:19.806719Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:39:47.179306Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:50:57.977337Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:52:18.888079Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_76_MINER-10-102-1-76.txt
10.102.1.77 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-16T16:24:49.351669Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:24:49.365296Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T16:26:06.214969Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:26:06.224196Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T16:37:09.142676Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:37:09.152012Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T16:38:26.015077Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:38:26.024228Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T17:39:27.925684Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T17:39:27.935268Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T17:40:45.302604Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T17:40:45.311658Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_77_MINER-10-102-1-77.txt

## 无算力
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.150 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 总线/通信异常；算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,3 | 2026-04-24T18:45:25.185110Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 550 chips, expected maximum 110 chips on one chain 2026-04-24T18:47:37.406915Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:53:44.892479Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(2)] 2026-04-24T18:56:09.372264Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T19:09:15.127351Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T19:13:41.057030Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 383 chips, expected maximum 110 chips on one chain ========== errors（错误） ========== 2015-01-01T00:00:39.276118Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) 2015-01-01T00:00:39.294576Z [ERROR] Failed to resolve ("btc.poolbinance.com", 1800) 2015-01-01T00:00:59.302343Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2015-01-01T00:00:59.517275Z [ERROR] Sensor hb2.73 probing failed: Setting pointer register to 0x07 for I2c read of 1 bytes: No such device or address (os error 6) 2015-01-01T00:00:59.555254Z [ERROR] Sensor hb3.74 probing failed: Setting pointer register to 0x07 for I2c read of 1 bytes: No such device or address (os error 6) | logs_10_102_0_150_MINER-10-102-0-150.txt
10.102.0.151 | 无算力(近零<= 2.00TH/s) | 0.090040 | 算力板部分失效（芯片数量严重不足） | 高 | 算力板/芯片异常；网络/矿池连接异常 | 算力板/芯片异常；网络/矿池连接异常 | 定位异常算力板并单板测试；检查该板排线、供电及散热状态；复位或升级固件后复测芯片识别数量；若芯片长期缺失，安排维修或更换算力板；当前日志涉及 HB:1 |  | logs_10_102_0_151_MINER-10-102-0-151.txt
10.102.0.155 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-27T02:45:49.720743Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T02:45:49.729842Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T02:47:17.588359Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T02:47:17.597507Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T02:48:51.568768Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T02:48:51.577822Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T02:50:26.740918Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T02:50:26.750226Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T02:56:44.467952Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T02:56:44.477887Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T02:57:54.689569Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T02:57:54.702605Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_155_MINER-10-102-0-155.txt
10.102.0.156 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,3 |  | logs_10_102_0_156_MINER-10-102-0-156.txt
10.102.0.157 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-26T21:08:35.079058Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:10:53.305623Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 13 (expected: 0x1366 received: 0x3) 2026-04-26T21:22:00.902846Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 13 (expected: 0x1366 received: 0x7f) 2026-04-26T21:24:13.325100Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:34:46.206240Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 16 (expected: 0x1366 received: 0x20) 2026-04-26T21:36:09.896950Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:38:28.631521Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:40:20.582686Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 16 (expected: 0x1366 received: 0x1004) 2026-04-26T21:51:31.897556Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 13 (expected: 0x1366 received: 0xe03) 2026-04-26T21:52:58.825350Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T22:47:43.703226Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 13 (expected: 0x1366 received: 0x0) 2026-04-26T22:49:16.349931Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_157_MINER-10-102-0-157.txt
10.102.0.158 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 网络/矿池连接异常；算力板/芯片异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 |  | logs_10_102_0_158_MINER-10-102-0-158.txt
10.102.0.176 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-24T19:55:28.846082Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T19:56:52.548670Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T20:59:27.157328Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:00:47.793588Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:02:57.179757Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:04:22.015704Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:15:33.584417Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:17:02.641700Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T22:18:12.868505Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T22:19:33.265558Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-25T12:11:13.128633Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-25T12:12:20.545010Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_176_MINER-10-102-0-176.txt
10.102.0.178 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-27T03:48:03.004348Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:49:14.066981Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:49:14.080605Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:50:30.928781Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:50:30.937916Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:55:36.485470Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:55:36.494631Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:57:36.545757Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:57:36.555342Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:58:50.566708Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:58:50.575987Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T04:00:05.334328Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_0_178_MINER-10-102-0-178.txt
10.102.0.182 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-27T01:08:06.828046Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:09:27.304339Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:50:27.174912Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:51:36.243437Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:53:04.534778Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:54:31.275912Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:05:31.989442Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:06:40.688727Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:13:49.677526Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:14:58.734854Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:16:06.968971Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:17:33.295446Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_182_MINER-10-102-0-182.txt
10.102.0.183 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T20:23:07.795022Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:25:28.502290Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:26:49.004945Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:36:36.065160Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:38:06.435571Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:39:26.866391Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:41:48.345368Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:52:58.471689Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:54:17.616898Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:57:05.204370Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:59:12.307797Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:00:31.882966Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_183_MINER-10-102-0-183.txt
10.102.0.184 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T21:51:54.399776Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:48:12.685709Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:49:33.299363Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:50:57.005296Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:52:23.338739Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:03:34.540893Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:05:03.554082Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:50:49.233591Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:52:09.860077Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:53:38.856977Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:54:58.876194Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T00:06:08.169319Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_184_MINER-10-102-0-184.txt
10.102.0.187 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-27T06:03:47.131218Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:03:50.912796Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:03:54.695924Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:03:58.481592Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:02.264388Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:06.046984Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:09.829839Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:13.615074Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:17.396650Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:21.178424Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:24.961794Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T06:04:28.743880Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) | logs_10_102_0_187_MINER-10-102-0-187.txt
10.102.0.190 | 无算力(近零<= 2.00TH/s) | 0.164411 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-24T15:11:51.063364Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:13:03.576947Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:14:20.741568Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T15:15:40.854094Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T15:18:13.781429Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:19:34.232196Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:20:40.740036Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T15:21:59.792715Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T15:33:13.858563Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:34:27.682169Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:41:39.716949Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:44:18.854463Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_190_MINER-10-102-0-190.txt
10.102.0.191 | 无算力(近零<= 2.00TH/s) | 1.316238 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2 | 2026-04-15T23:44:42.360430Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T14:12:02.961961Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T14:13:43.041980Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 11 (expected: 0x1366 received: 0xd00) 2026-04-16T19:29:31.053982Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T22:57:49.241626Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:55:08.309141Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:57:26.595112Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:41:46.729661Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain ========== errors（错误） ========== 2015-01-01T00:00:39.436262Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) 2015-01-01T00:00:59.456349Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2015-01-01T00:01:08.891236Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) | logs_10_102_0_191_MINER-10-102-0-191.txt
10.102.0.192 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T21:34:45.235844Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:36:08.932820Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:37:29.640569Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:38:55.925427Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:50:06.372967Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:51:27.036423Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:47:43.794770Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:49:04.405283Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:50:25.040725Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:51:46.199483Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:02:57.118249Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:04:18.921479Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_192_MINER-10-102-0-192.txt
10.102.0.193 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-27T01:51:37.173079Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:52:52.168615Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:54:11.202688Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:05:12.088183Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:06:19.803406Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:13:49.599211Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:14:58.657972Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:16:06.908631Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:17:18.514875Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:21:25.870816Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:22:34.931067Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:23:43.220573Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_193_MINER-10-102-0-193.txt
10.102.0.194 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-27T02:19:33.728213Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T02:21:26.866662Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:22:35.930584Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:23:49.855230Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:25:10.379262Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:36:09.581650Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:37:16.995135Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T02:40:17.745914Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T02:40:27.262816Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T02:40:36.788445Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T02:40:46.306236Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T02:42:07.756431Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_194_MINER-10-102-0-194.txt
10.102.0.195 | 无算力(0TH/s) | 0.001248 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2 | 2026-04-27T19:22:07.981848Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:11.761223Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:15.539777Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:19.316390Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:23.094066Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:26.872426Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:30.650158Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:34.427743Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:38.206302Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:41.983237Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:45.762293Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T19:22:49.539896Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) | logs_10_102_0_195_MINER-10-102-0-195.txt
10.102.0.197 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-27T13:03:28.744477Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:03:33.886190Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:03:39.031117Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:03:44.172706Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:03:49.313991Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:03:54.457426Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:03:59.597346Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:04:04.764712Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:04:09.908898Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:04:15.052396Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:04:20.193766Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:04:25.337452Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_197_MINER-10-102-0-197.txt
10.102.0.198 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2 | 2026-04-26T19:07:08.234538Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T19:09:01.767539Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-26T19:11:32.599630Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-26T19:22:58.868385Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T19:25:32.859372Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T19:42:53.964887Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T19:46:52.235074Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T19:49:19.685201Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T19:51:32.722732Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-26T19:54:23.477030Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-26T20:05:47.962514Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:08:14.628183Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_198_MINER-10-102-0-198.txt
10.102.0.199 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T19:52:04.473850Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:03:15.788975Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:04:49.091827Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:11:19.623849Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:12:52.235346Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:14:21.977926Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:15:53.913548Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:21:42.879143Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:23:15.533618Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:24:45.254035Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:26:12.388668Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:36:52.135969Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_199_MINER-10-102-0-199.txt
10.102.0.202 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-24T18:02:28.278721Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:14:28.463380Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:16:16.272537Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:37:29.071435Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:39:29.139989Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:00:07.124030Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:22:13.914159Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:24:20.495585Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:28:33.695546Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(3)] 2026-04-26T20:35:20.170651Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-26T20:47:16.386278Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:48:40.815600Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_202_MINER-10-102-0-202.txt
10.102.0.206 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-25T12:09:36.407445Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-25T12:10:45.978957Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-25T12:12:36.282164Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-25T12:15:06.814754Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-25T12:26:28.356370Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-25T12:27:39.201000Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-25T13:28:51.269749Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-25T13:30:05.432111Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-25T19:31:15.162183Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-25T19:32:42.891122Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-25T19:53:53.212743Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-25T19:55:26.338239Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_206_MINER-10-102-0-206.txt
10.102.0.208 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-20T07:53:46.847864Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I2} detected 437 chips, expected maximum 110 chips on one chain 2026-04-20T17:03:10.260051Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-21T02:40:56.528781Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:53:44.204086Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T04:24:45.860536Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:13:02.600034Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:21:36.405075Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T18:18:30.025302Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-22T02:15:37.786314Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-22T11:05:47.035661Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-22T14:49:23.279039Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T06:49:04.228294Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 23 (expected: 0x1366 received: 0xd47) | logs_10_102_0_208_MINER-10-102-0-208.txt
10.102.0.209 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 总线/通信异常；算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-22T14:48:51.791483Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-22T15:28:13.698439Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 494 chips, expected maximum 110 chips on one chain 2026-04-22T15:29:21.117328Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-22T15:37:15.770564Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 503 chips, expected maximum 110 chips on one chain 2026-04-22T20:51:32.386809Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-23T00:21:58.360707Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-23T01:29:54.097606Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 117 chips, expected maximum 110 chips on one chain 2026-04-23T01:31:39.820170Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-23T02:36:09.342880Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-23T02:45:33.596010Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 550 chips, expected maximum 110 chips on one chain 2026-04-23T04:53:37.711934Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 215 chips, expected maximum 110 chips on one chain 2026-04-23T04:54:57.534288Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_209_MINER-10-102-0-209.txt
10.102.0.210 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:2,3 | 2026-04-15T23:44:05.584004Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-15T23:45:24.870014Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T14:12:07.658118Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T14:13:14.582528Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T19:22:06.303979Z [ERROR] Tuner error: Stage 4: Stage 4: Zero MCR on hashboards [Address(1)] 2026-04-16T19:27:09.319707Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T19:28:30.536220Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:55:08.526754Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:56:33.551728Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:57:27.016490Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:58:38.229884Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:54:08.750536Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_210_MINER-10-102-0-210.txt
10.102.0.211 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-19T17:39:31.326342Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 1284 chips, expected maximum 110 chips on one chain 2026-04-21T12:37:18.811036Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1), Address(2), Address(3)] 2026-04-21T12:57:38.325966Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(1), Address(2), Address(3)] 2026-04-21T13:18:38.706221Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2), Address(3)] 2026-04-21T13:37:50.806157Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2), Address(3)] 2026-04-21T14:06:30.611478Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2), Address(3)] 2026-04-21T14:07:55.733509Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:08:58.428932Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:12:54.269367Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T15:31:48.468257Z [ERROR] Tuner error: Stage Some(13): restart: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:06:28.750036Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-21T16:35:34.662059Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 3 (expected: 0x1366 received: 0x16ff) | logs_10_102_0_211_MINER-10-102-0-211.txt
10.102.0.215 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-26T21:04:00.091437Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:05:29.444169Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-26T21:06:50.935007Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:08:17.979733Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:19:32.558110Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:20:54.427683Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-26T21:34:46.622319Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:36:07.256417Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-26T21:37:28.664390Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:38:55.141443Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:50:04.847389Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-26T21:51:25.349495Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) | logs_10_102_0_215_MINER-10-102-0-215.txt
10.102.0.217 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-27T13:24:54.139496Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:24:59.282076Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:04.458640Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:09.603903Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:14.746708Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:19.891783Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:25.036873Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:30.181174Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:35.325947Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:40.469070Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:45.645235Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-27T13:25:50.786745Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_217_MINER-10-102-0-217.txt
10.102.0.218 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-27T03:10:48.296852Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:10:52.183952Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:10:56.071024Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:10:59.960516Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:03.848595Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:07.735420Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:11.623146Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:15.511187Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:19.398661Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:23.288223Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:27.174647Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-27T03:11:31.062555Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) | logs_10_102_0_218_MINER-10-102-0-218.txt
10.102.0.220 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-24T15:44:22.267446Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:46:31.792257Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:51:32.788042Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-04-24T15:52:51.448308Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T15:54:07.341873Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T16:05:39.810283Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T16:12:41.644173Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T17:10:06.541877Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x0) 2026-04-24T17:11:33.242512Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T17:13:40.491776Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T17:25:05.538390Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T17:50:25.044038Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_220_MINER-10-102-0-220.txt
10.102.0.223 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 读取失败（多链初始化失败，SOC 无法启动） | 高 | 矿机服务异常/接口超时；多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 根据 load chain … eeprom / Data load fail / eeprom load ret:-1 定位失败链；逐链重插数据排线与电源，换槽位交叉测试区分板卡与控制板；EEPROM error: CRC … REGION、Fixture data load failed 多为数据损坏或通信问题；多链同时失败优先查共因（排线、控制板 EEPROM 通路、固件版本）；出现 ERROR_SOC_INIT: basic init failed / stop_mining: basic init failed 时，勿先当总线泛化故障；可尝试重刷官方或兼容固件后再测；若单链异常可换板；多链皆失败且排除连接后重点考虑控制板或批量硬件问题 | [ 0.527257@0] clkmsr ffd18004.meson_clk_msr: failed to get msr ring reg0 [ 0.646373@0] dmi: Firmware registration failed. [ 1.518589@0] Initramfs unpacking failed: junk in compressed archive [ 2.021667@3] i2c i2c-1: of_i2c: modalias failure on /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 2.025474@3] i2c i2c-1: Failed to create I2C device for /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 3.185931@0] defendkey: probe of defendkey failed with error -22 [ 3.934175@1] hub 2-0:1.0: config failed, hub doesn't have any ports! (err -19) [ 4.099850@1] thermal thermal_zone0: binding zone soc_thermal with cdev thermal-cpufreq-0 failed:-22 [ 5.767015@0] meson6-dwmac ff3f0000.ethernet eth0: fail to init PTP. 2026-04-27 08:25:12 get test_loop_securely_find_asic_num failed 2026-04-27 08:25:18 fail to write 0:1 2026-04-27 08:25:18 fail to read 0:1 | logs_10_102_0_223_MINER-10-102-0-223.txt
10.102.1.61 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-27T04:21:52.234303Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:01.746706Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:11.266750Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:20.782708Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:30.300567Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:39.816752Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:49.330389Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:22:58.850620Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:23:08.370482Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:23:17.886800Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:23:27.413465Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded 2026-04-27T04:23:36.947975Z [ERROR] Mining backend: {ERR:E4} Cannot start miner when some hashboard EEPROMs could not be decoded | logs_10_102_1_61_MINER-10-102-1-61.txt
10.102.1.62 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T20:03:57.462748Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:05:40.808932Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:10:59.555607Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:12:40.098440Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:14:33.926242Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:16:23.290195Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:21:38.757638Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:23:21.157215Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:25:11.412288Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:26:56.124564Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:36:36.032624Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:38:25.429258Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_62_MINER-10-102-1-62.txt
10.102.1.63 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T21:36:06.727145Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:37:36.743836Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:38:58.331714Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:50:05.863126Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:51:25.496948Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:47:43.767537Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:49:05.414763Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:50:34.780054Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:52:02.220171Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:03:13.723531Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:04:35.341568Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:50:19.980077Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_63_MINER-10-102-1-63.txt
10.102.1.64 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-24T07:33:43.700982Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T07:44:44.427934Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T07:45:53.750141Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T08:46:51.180063Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T08:48:00.232658Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T13:27:07.344951Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T13:28:16.400416Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T13:29:36.682072Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T13:31:15.573848Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T13:42:21.015997Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 4 (expected: 0x1366 received: 0x1040) 2026-04-24T13:43:34.437274Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:32:35.639838Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 122 chips, expected maximum 110 chips on one chain | logs_10_102_1_64_MINER-10-102-1-64.txt
10.102.1.65 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T22:49:06.086522Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:52:17.808717Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:53:41.211642Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:04:50.378187Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:07:39.507018Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:50:21.030849Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:53:24.812105Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:54:51.110347Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T23:57:51.714423Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T00:09:01.448307Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T00:11:55.036838Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T01:12:53.741160Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_65_MINER-10-102-1-65.txt
10.102.1.66 | 无算力(近零<= 2.00TH/s) | 0.227468 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-12T07:49:23.282759Z [ERROR] Tuner error: Stage Some(13): restart: Disabled hashboard 3 {HB:3}: {ERR:I2} detected 567 chips, expected maximum 110 chips on one chain 2026-04-13T02:33:04.841753Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1), Address(2), Address(3)] 2026-04-14T03:07:41.442005Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 91 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T03:08:48.328939Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 7 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:01:36.693693Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 91 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:02:45.327352Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 7 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:04:05.207852Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 109 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:05:45.133862Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 91 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:16:42.023726Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 91 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing 2026-04-14T04:17:48.909650Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: Hashchip: number of responses 7 of read_register(reg=0x0) doesn't match chip count 110: reply 0x2 missing ========== errors（错误） ========== 2026-04-05T21:46:38.116882Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) | logs_10_102_1_66_MINER-10-102-1-66.txt
10.102.1.67 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-27T03:14:21.577947Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:17:39.620258Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:17:39.629413Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:18:55.629569Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:18:55.638943Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:20:09.977174Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:20:09.990002Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:21:26.981116Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:21:26.990196Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:33:08.397509Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:33:08.406789Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:34:24.406479Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_1_67_MINER-10-102-1-67.txt
10.102.1.72 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-27T03:12:38.643271Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:12:38.652289Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:15:21.303153Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:15:21.312375Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:16:31.647452Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:16:31.658734Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:17:45.466847Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:17:45.476973Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:19:02.723045Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:19:02.732397Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:30:05.815573Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:30:05.825122Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_72_MINER-10-102-1-72.txt
10.102.1.73 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-24T18:40:22.356784Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T19:51:47.622361Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-24T20:17:35.803245Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T20:19:44.259293Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:41:37.359696Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:43:10.804105Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:50:19.174522Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:52:23.406443Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T22:34:57.843080Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-24T23:34:23.390659Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-24T23:36:25.783262Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-25T12:14:48.341029Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(1)] | logs_10_102_1_73_MINER-10-102-1-73.txt
10.102.1.75 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-27T03:48:57.582458Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:51:21.521755Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:51:21.528590Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:52:35.614986Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:52:35.621489Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:53:46.847633Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:53:46.854145Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:55:26.538187Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:55:26.545283Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:57:26.597949Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-27T03:57:26.604673Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-27T03:58:40.769354Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_1_75_MINER-10-102-1-75.txt
10.102.1.76 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-26T20:13:38.766514Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:15:02.489832Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:21:38.790891Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:23:01.508529Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:24:20.586133Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:25:49.812890Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:35:37.414460Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:36:59.304094Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:38:19.806719Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:39:47.179306Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:50:57.977337Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-26T20:52:18.888079Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_76_MINER-10-102-1-76.txt
10.102.1.77 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 网络/矿池连接异常；算力板/芯片异常；总线/通信异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-16T16:24:49.351669Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:24:49.365296Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T16:26:06.214969Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:26:06.224196Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T16:37:09.142676Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:37:09.152012Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T16:38:26.015077Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T16:38:26.024228Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T17:39:27.925684Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T17:39:27.935268Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-16T17:40:45.302604Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-16T17:40:45.311658Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_1_77_MINER-10-102-1-77.txt

## 低算力
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.162 | 低算力(<50TH/s) | 39.050030 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-04-28T12:57:17.556941Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:19.154312Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:20.747039Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:22.344673Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:23.946166Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:25.541377Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:27.138960Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:28.736411Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:30.339119Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:31.934235Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:33.531794Z [WARN] Temperature Sensor Read Failed 2026-04-28T12:57:35.129274Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_162_MINER-10-102-0-162.txt
10.102.0.174 | 低算力(<50TH/s) | 36.779636 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-07T21:10:08.476864Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-07T21:15:16.995517Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T02:36:18.878485Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T03:06:02.077325Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T18:20:36.462137Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:16:12.772087Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-11T10:17:36.726948Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:33:21.335733Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:30.532566Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:36:12.111990Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-12T07:38:31.749507Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-12T08:46:39.169679Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_174_MINER-10-102-0-174.txt
10.102.0.179 | 低算力(<50TH/s) | 46.571303 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；电源异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,3 | 2026-04-10T23:16:34.685589Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-10T23:18:19.532950Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-11T12:10:21.954887Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-11T12:11:30.907960Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-12T07:34:05.253515Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-12T07:37:57.811006Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-12T23:23:00.354405Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-12T23:24:19.565920Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:34:06.426416Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-13T01:35:15.979449Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-13T19:16:23.328355Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-04-13T19:17:44.536601Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_179_MINER-10-102-0-179.txt
10.102.0.213 | 低算力(<50TH/s) | 46.409840 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 网络/矿池连接异常；算力板/芯片异常；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-15T23:42:54.112824Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-15T23:44:36.223520Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T14:12:32.171279Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-16T14:13:45.428336Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T19:29:13.137255Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-16T19:30:38.371121Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:55:07.436139Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:56:34.691817Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:57:18.820070Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:58:28.392112Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:54:08.697631Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:18.271886Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_213_MINER-10-102-0-213.txt
10.102.0.216 | 低算力(<50TH/s) | 40.328792 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:2,3 | 2026-04-26T07:38:19.305455Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:24.559131Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:29.813314Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:35.069519Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:40.323413Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:45.575877Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:50.829303Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:38:56.088056Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:39:01.342124Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:39:06.595887Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:39:11.852336Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-26T07:39:17.106776Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_216_MINER-10-102-0-216.txt