## 全部异常
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.150 | 无算力(近零<= 2.00TH/s) | 0.126297 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 总线/通信异常；算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,3 | 2026-04-24T18:45:25.185110Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 550 chips, expected maximum 110 chips on one chain 2026-04-24T18:47:37.406915Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:53:44.892479Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(2)] 2026-04-24T18:56:09.372264Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T19:09:15.127351Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T19:13:41.057030Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 383 chips, expected maximum 110 chips on one chain ========== errors（错误） ========== 2015-01-01T00:00:39.276118Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) 2015-01-01T00:00:39.294576Z [ERROR] Failed to resolve ("btc.poolbinance.com", 1800) 2015-01-01T00:00:59.302343Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2015-01-01T00:00:59.517275Z [ERROR] Sensor hb2.73 probing failed: Setting pointer register to 0x07 for I2c read of 1 bytes: No such device or address (os error 6) 2015-01-01T00:00:59.555254Z [ERROR] Sensor hb3.74 probing failed: Setting pointer register to 0x07 for I2c read of 1 bytes: No such device or address (os error 6) | logs_10_102_0_150_MINER-10-102-0-150.txt
10.102.0.151 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时 | 算力板/芯片异常；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1 | 2026-04-24T17:57:22.154018Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:08:34.298415Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:09:56.022551Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:24:21.449414Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:26:35.482781Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:29:41.319742Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2), Address(3)] 2026-04-24T18:31:15.919867Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:36:56.521819Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:38:16.738035Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:41:17.148446Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:44:33.443639Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:56:02.142847Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_151_MINER-10-102-0-151.txt
10.102.0.155 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-05-01T01:48:35.366227Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:48:35.375487Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:49:52.465921Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:49:52.474948Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:59:21.139071Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:59:21.148351Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T02:00:31.340438Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:00:31.349917Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T02:01:45.089090Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:01:45.101569Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T02:03:02.139781Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:03:02.148678Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_155_MINER-10-102-0-155.txt
10.102.0.156 | 无算力(近零<= 2.00TH/s) | 0.350929 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,3 |  | logs_10_102_0_156_MINER-10-102-0-156.txt
10.102.0.158 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 |  | logs_10_102_0_158_MINER-10-102-0-158.txt
10.102.0.162 | 低算力(<50TH/s) | 47.771210 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-05-03T06:15:33.775808Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:35.371281Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:36.968744Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:38.568432Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:40.161526Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:41.759173Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:43.358797Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:44.956372Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:46.551508Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:48.149177Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:49.748898Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:51.344112Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_162_MINER-10-102-0-162.txt
10.102.0.174 | 低算力(<50TH/s) | 36.177077 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-16T19:30:23.989661Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T22:57:33.626113Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T22:58:58.830976Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:54:48.639817Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:56:09.860848Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:57:41.699354Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:58:49.638738Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:41:24.237540Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:42:33.820194Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:54:12.974860Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:24.401498Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:39:37.311693Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_174_MINER-10-102-0-174.txt
10.102.0.176 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-28T20:51:45.205835Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:54:18.951229Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:59:06.446397Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:00:27.115513Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:02:37.468679Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:03:58.176284Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:15:08.852921Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:16:28.841356Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:03:05.165192Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:04:34.539178Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:06:48.009211Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:08:06.482409Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_176_MINER-10-102-0-176.txt
10.102.0.179 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-18T09:54:44.896945Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:54.446994Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:39:23.382869Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:40:35.069623Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-20T17:03:10.427759Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-21T02:54:35.592699Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:55:49.863735Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T04:25:17.899851Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T04:26:32.234363Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:22:30.163629Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:23:43.459988Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T18:19:32.034143Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_179_MINER-10-102-0-179.txt
10.102.0.187 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-29T03:48:06.756586Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:10.536756Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:14.316039Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:18.096870Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:21.877402Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:25.657955Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:30.809137Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-29T03:48:34.589976Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:38.369557Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:42.150103Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:45.929772Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:49.709911Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) | logs_10_102_0_187_MINER-10-102-0-187.txt
10.102.0.190 | 无算力(近零<= 2.00TH/s) | 0.117063 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-24T18:36:59.747032Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:38:26.634700Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:40:11.963393Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T18:41:29.434976Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T18:52:52.730448Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:54:19.983780Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T19:55:32.727823Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T19:57:05.928332Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T20:59:27.504163Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:00:47.357333Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:02:46.861093Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T21:04:05.841090Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] | logs_10_102_0_190_MINER-10-102-0-190.txt
10.102.0.191 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-18T09:54:18.758862Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:27.122734Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:47:25.281505Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-19T12:38:16.904303Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-19T17:39:52.519645Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:41:05.368465Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T16:58:16.916641Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-20T17:03:02.934401Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-20T20:23:10.328852Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-21T02:54:44.451108Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:55:57.191647Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T04:25:25.809303Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_191_MINER-10-102-0-191.txt
10.102.0.192 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-28T19:37:36.521802Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:49:03.965868Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:50:24.810026Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:51:44.469936Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:53:53.864439Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:59:04.489909Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:00:33.829958Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:02:00.533684Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:03:26.056129Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:14:37.162698Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:15:58.829474Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:03:06.149063Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_192_MINER-10-102-0-192.txt
10.102.0.193 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-27T06:41:39.410973Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:23:01.360853Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:24:10.427296Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:26:32.465444Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:27:41.531133Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:28:49.816523Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:30:01.372691Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:40:58.803457Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:42:07.863699Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T09:43:11.877596Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T09:44:20.926571Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T15:45:18.363420Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_193_MINER-10-102-0-193.txt
10.102.0.194 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-05-03T06:12:11.340013Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:16.493531Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:21.646853Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:26.830690Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:31.983288Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:37.137380Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:42.290732Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:47.442256Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:52.626947Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:57.781859Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:13:02.935565Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:13:08.090697Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_194_MINER-10-102-0-194.txt
10.102.0.197 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-05-02T12:06:58.173493Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:03.315802Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:08.481117Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:13.622269Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:18.763758Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:23.929725Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:29.072409Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:34.215746Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:39.359192Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:44.503664Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:49.646687Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:54.791364Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_197_MINER-10-102-0-197.txt
10.102.0.199 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-28T20:50:49.857786Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:52:20.016112Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:53:44.858405Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:59:20.596698Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:00:49.953611Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:02:15.489350Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:04:55.016231Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:16:06.898946Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:17:40.806346Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:03:21.309438Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:04:56.271022Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:06:23.753755Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_199_MINER-10-102-0-199.txt
10.102.0.206 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-27T05:53:05.716178Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:23:35.992977Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:24:45.568565Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T09:19:47.878858Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-27T09:27:53.258254Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-27T09:39:09.355748Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T09:40:21.862303Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T10:41:22.035678Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T10:42:31.595117Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T16:43:41.537438Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T16:45:08.972706Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T22:46:18.067072Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_206_MINER-10-102-0-206.txt
10.102.0.208 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-26T20:50:49.422581Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(1)] 2026-04-26T21:02:45.351130Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:12:49.019968Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(3)] 2026-04-26T21:35:11.832684Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:37:53.843025Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I1} unexpected revision of chip 3 (expected: 0x1366 received: 0xc30) 2026-04-26T21:46:41.075901Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(1)] 2026-04-26T21:57:21.176302Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(1)] 2026-04-26T22:09:17.428824Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:12:07.320714Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I1} unexpected revision of chip 3 (expected: 0x1366 received: 0x630) 2026-04-26T22:48:12.404990Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 199 chips, expected maximum 110 chips on one chain 2026-04-26T22:50:44.519111Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:52:17.593671Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_208_MINER-10-102-0-208.txt
10.102.0.210 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-25T15:20:14.670396Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T03:39:37.390801Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T03:48:45.034210Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-04-26T20:53:10.297842Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:13:48.379556Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I2} detected 468 chips, expected maximum 110 chips on one chain 2026-04-27T05:34:37.661275Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 1 (expected: 0x1366 received: 0x2) 2026-04-27T05:35:45.594962Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T16:42:35.528444Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-27T18:20:03.821960Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-27T19:52:44.252992Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-27T20:37:39.441451Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-27T20:49:28.911208Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_210_MINER-10-102-0-210.txt
10.102.0.211 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-27T04:12:57.778511Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:42:42.194864Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:43:51.252720Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:44:59.524491Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:46:11.159208Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:53:53.921913Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:26:56.242568Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:27:59.491342Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1), Address(3)] 2026-04-28T03:54:06.803347Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-28T04:33:36.705168Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-28T04:34:40.756466Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-28T06:53:54.311165Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] | logs_10_102_0_211_MINER-10-102-0-211.txt
10.102.0.213 | 低算力(<50TH/s) | 41.460135 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-15T23:42:54.112824Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-15T23:44:36.223520Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T14:12:32.171279Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-16T14:13:45.428336Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T19:29:13.137255Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-16T19:30:38.371121Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:55:07.436139Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:56:34.691817Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:57:18.820070Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:58:28.392112Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:54:08.697631Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:18.271886Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_213_MINER-10-102-0-213.txt
10.102.0.215 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-29T02:59:16.004584Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T03:10:13.984571Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T03:11:23.059395Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-29T03:44:55.839113Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T03:46:04.912107Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-29T03:47:13.177843Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T03:48:24.757807Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T03:59:23.129495Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T04:00:32.201363Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-29T05:01:37.833214Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T05:02:45.249582Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-29T11:03:42.679255Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_215_MINER-10-102-0-215.txt
10.102.0.216 | 低算力(<50TH/s) | 30.372106 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；矿机服务异常/接口超时；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:2,3 | 2026-05-03T06:01:07.431145Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:12.587302Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:17.739081Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:22.891793Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:28.044160Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:33.197445Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:38.350929Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:43.506386Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:48.661004Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:53.813861Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:58.968670Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:02:04.124018Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_216_MINER-10-102-0-216.txt
10.102.0.217 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-05-01T17:40:27.744456Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:40:32.884702Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:40:38.032809Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:40:43.173120Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:40:48.313401Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:40:53.453278Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:40:58.593653Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:41:03.739134Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:41:08.882852Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:41:14.026021Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:41:19.196449Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:41:24.335328Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_217_MINER-10-102-0-217.txt
10.102.0.221 | 无算力(0TH/s) | 0.000000 | 温度传感器通信失败（误报超温/温差保护停机） | 高 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-05-03T06:16:56.517324Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:16:58.114488Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:16:59.711690Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:17:01.313297Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:17:02.910267Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:17:04.371168Z [ERROR] connection dropped due to pool inactivity 2026-05-03T06:17:04.371407Z [ERROR] Stratum read failure 2026-05-03T06:17:04.372050Z [INFO] Connection closed by the server 2026-05-03T06:17:04.502942Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:17:06.100277Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:17:07.699753Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:17:09.298989Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_221_MINER-10-102-0-221.txt
10.102.0.223 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 读取失败（多链初始化失败，SOC 无法启动） | 高 | 矿机服务异常/接口超时；多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 根据 load chain … eeprom / Data load fail / eeprom load ret:-1 定位失败链；逐链重插数据排线与电源，换槽位交叉测试区分板卡与控制板；EEPROM error: CRC … REGION、Fixture data load failed 多为数据损坏或通信问题；多链同时失败优先查共因（排线、控制板 EEPROM 通路、固件版本）；出现 ERROR_SOC_INIT: basic init failed / stop_mining: basic init failed 时，勿先当总线泛化故障；可尝试重刷官方或兼容固件后再测；若单链异常可换板；多链皆失败且排除连接后重点考虑控制板或批量硬件问题 | [ 0.523180@0] clkmsr ffd18004.meson_clk_msr: failed to get msr ring reg0 [ 0.638304@0] dmi: Firmware registration failed. [ 1.510569@2] Initramfs unpacking failed: junk in compressed archive [ 2.007017@2] i2c i2c-1: of_i2c: modalias failure on /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 2.010797@2] i2c i2c-1: Failed to create I2C device for /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 3.168464@2] defendkey: probe of defendkey failed with error -22 [ 3.916668@2] hub 2-0:1.0: config failed, hub doesn't have any ports! (err -19) [ 4.082357@0] thermal thermal_zone0: binding zone soc_thermal with cdev thermal-cpufreq-0 failed:-22 [ 5.755531@0] meson6-dwmac ff3f0000.ethernet eth0: fail to init PTP. 2026-05-03 03:01:53 get test_loop_securely_find_asic_num failed 2026-05-03 03:02:00 fail to write 0:1 2026-05-03 03:02:00 fail to read 0:1 | logs_10_102_0_223_MINER-10-102-0-223.txt
10.102.1.62 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-28T20:49:04.958940Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:50:37.639838Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:52:14.271966Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:53:41.712140Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:59:05.833763Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:00:44.074190Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:02:13.161915Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:03:38.090724Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:14:49.126464Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:16:23.196131Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:03:06.100003Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:04:39.999790Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_62_MINER-10-102-1-62.txt
10.102.1.63 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-27T05:39:07.777553Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T06:40:07.360091Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T06:41:14.779538Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:23:02.493444Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:24:11.567509Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:25:19.836773Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:26:31.390949Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:37:29.534922Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:38:38.603649Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T09:39:42.601355Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T09:40:51.653321Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T15:41:49.073031Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_63_MINER-10-102-1-63.txt
10.102.1.64 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-27T13:11:51.097199Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T13:13:11.623861Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T14:26:59.486811Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 9 (expected: 0x1366 received: 0x0) 2026-04-27T15:32:50.425251Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 16 (expected: 0x1366 received: 0x426) 2026-04-27T15:35:38.193534Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T05:06:20.919702Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T05:07:39.763818Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T05:09:40.857483Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T06:14:38.329149Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T06:26:04.172828Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 3 (expected: 0x1366 received: 0x8) 2026-04-28T06:27:30.462745Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T07:28:53.682694Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 319 chips, expected maximum 110 chips on one chain | logs_10_102_1_64_MINER-10-102-1-64.txt
10.102.1.65 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-28T22:10:38.787927Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:21:51.789350Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:24:39.549848Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T23:25:48.641736Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T23:27:18.666830Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-29T02:55:47.837990Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-29T02:57:21.227542Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-29T02:59:26.725421Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-29T03:01:34.190945Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-29T03:12:34.080299Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-29T03:14:07.516503Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-29T03:44:55.790896Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_65_MINER-10-102-1-65.txt
10.102.1.67 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-30T16:17:58.000401Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-30T17:19:05.342690Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-30T17:19:05.351840Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-30T17:20:15.074812Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-30T17:20:15.087663Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T00:16:34.991085Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T00:16:35.001286Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T00:17:52.071092Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T00:17:52.080424Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:42:49.424403Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:42:49.433752Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:44:05.488245Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_1_67_MINER-10-102-1-67.txt
10.102.1.72 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-05-01T01:55:55.146453Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:55:55.155580Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 6 (expected: 0x1366 received: 0xf00) 2026-05-01T01:58:51.314795Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:58:51.324188Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 14 of read_register(reg=0x0) doesn't match chip count 110: reply 0x8 missing 2026-05-01T02:00:06.874955Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:00:06.885572Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-05-01T02:01:19.267298Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:01:19.276740Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-05-01T02:02:32.183061Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:02:32.192168Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-05-01T02:13:35.262516Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:13:35.275362Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) | logs_10_102_1_72_MINER-10-102-1-72.txt
10.102.1.73 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-27T04:23:17.102049Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:25:46.786397Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:26:56.372361Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:26:52.876398Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:28:04.493538Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T17:53:47.906170Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T17:55:15.906044Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T17:57:01.152437Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T17:59:14.124794Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T19:03:55.432228Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T19:05:30.365898Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T20:14:09.639870Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_73_MINER-10-102-1-73.txt
10.102.1.75 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-30T18:29:49.059456Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T00:30:51.961555Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T00:30:51.970821Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:28:05.299240Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:28:05.308347Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:42:10.585061Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:42:10.595242Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:43:26.679754Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:43:26.692512Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:45:53.289667Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:45:53.299174Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:47:07.326997Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_1_75_MINER-10-102-1-75.txt
10.102.1.77 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；总线/通信异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-17T01:57:41.425168Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:58:50.985511Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:41:29.180560Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:42:40.918876Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:54:45.228351Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:54.797216Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T12:38:30.128125Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T14:26:40.489845Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-19T14:51:58.049052Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-19T17:38:47.253381Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:39:56.836740Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-20T16:58:28.887090Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_77_MINER-10-102-1-77.txt

## 无算力
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.150 | 无算力(近零<= 2.00TH/s) | 0.126297 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 总线/通信异常；算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,3 | 2026-04-24T18:45:25.185110Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 550 chips, expected maximum 110 chips on one chain 2026-04-24T18:47:37.406915Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:53:44.892479Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(2)] 2026-04-24T18:56:09.372264Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T19:09:15.127351Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T19:13:41.057030Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 383 chips, expected maximum 110 chips on one chain ========== errors（错误） ========== 2015-01-01T00:00:39.276118Z [ERROR] Failed to resolve ("sha256.poolbinance.com", 443) 2015-01-01T00:00:39.294576Z [ERROR] Failed to resolve ("btc.poolbinance.com", 1800) 2015-01-01T00:00:59.302343Z [ERROR] Failed to resolve ("a830bcc3.bos.braiins.com", 3336) 2015-01-01T00:00:59.517275Z [ERROR] Sensor hb2.73 probing failed: Setting pointer register to 0x07 for I2c read of 1 bytes: No such device or address (os error 6) 2015-01-01T00:00:59.555254Z [ERROR] Sensor hb3.74 probing failed: Setting pointer register to 0x07 for I2c read of 1 bytes: No such device or address (os error 6) | logs_10_102_0_150_MINER-10-102-0-150.txt
10.102.0.151 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时 | 算力板/芯片异常；网络/矿池连接异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1 | 2026-04-24T17:57:22.154018Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:08:34.298415Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:09:56.022551Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:24:21.449414Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:26:35.482781Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:29:41.319742Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2), Address(3)] 2026-04-24T18:31:15.919867Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:36:56.521819Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:38:16.738035Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:41:17.148446Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:44:33.443639Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-24T18:56:02.142847Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_151_MINER-10-102-0-151.txt
10.102.0.155 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-05-01T01:48:35.366227Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:48:35.375487Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:49:52.465921Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:49:52.474948Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:59:21.139071Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:59:21.148351Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T02:00:31.340438Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:00:31.349917Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T02:01:45.089090Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:01:45.101569Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T02:03:02.139781Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:03:02.148678Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_155_MINER-10-102-0-155.txt
10.102.0.156 | 无算力(近零<= 2.00TH/s) | 0.350929 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,3 |  | logs_10_102_0_156_MINER-10-102-0-156.txt
10.102.0.158 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 |  | logs_10_102_0_158_MINER-10-102-0-158.txt
10.102.0.176 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-28T20:51:45.205835Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:54:18.951229Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:59:06.446397Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:00:27.115513Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:02:37.468679Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:03:58.176284Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:15:08.852921Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:16:28.841356Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:03:05.165192Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:04:34.539178Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:06:48.009211Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:08:06.482409Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_176_MINER-10-102-0-176.txt
10.102.0.179 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-18T09:54:44.896945Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:54.446994Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:39:23.382869Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:40:35.069623Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-20T17:03:10.427759Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-21T02:54:35.592699Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:55:49.863735Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T04:25:17.899851Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T04:26:32.234363Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:22:30.163629Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T16:23:43.459988Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-21T18:19:32.034143Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_179_MINER-10-102-0-179.txt
10.102.0.187 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-04-29T03:48:06.756586Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:10.536756Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:14.316039Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:18.096870Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:21.877402Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:25.657955Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:30.809137Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-04-29T03:48:34.589976Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:38.369557Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:42.150103Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:45.929772Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) 2026-04-29T03:48:49.709911Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 1: No such device or address (os error 6) | logs_10_102_0_187_MINER-10-102-0-187.txt
10.102.0.190 | 无算力(近零<= 2.00TH/s) | 0.117063 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-24T18:36:59.747032Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:38:26.634700Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:40:11.963393Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T18:41:29.434976Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T18:52:52.730448Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T18:54:19.983780Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T19:55:32.727823Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T19:57:05.928332Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T20:59:27.504163Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:00:47.357333Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-24T21:02:46.861093Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-24T21:04:05.841090Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] | logs_10_102_0_190_MINER-10-102-0-190.txt
10.102.0.191 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-18T09:54:18.758862Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:27.122734Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T03:47:25.281505Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-19T12:38:16.904303Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-19T17:39:52.519645Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:41:05.368465Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-20T16:58:16.916641Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-20T17:03:02.934401Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-20T20:23:10.328852Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-21T02:54:44.451108Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-21T02:55:57.191647Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-21T04:25:25.809303Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_191_MINER-10-102-0-191.txt
10.102.0.192 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-28T19:37:36.521802Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:49:03.965868Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:50:24.810026Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:51:44.469936Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:53:53.864439Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:59:04.489909Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:00:33.829958Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:02:00.533684Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:03:26.056129Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:14:37.162698Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:15:58.829474Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:03:06.149063Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_192_MINER-10-102-0-192.txt
10.102.0.193 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-27T06:41:39.410973Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:23:01.360853Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:24:10.427296Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:26:32.465444Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:27:41.531133Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:28:49.816523Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:30:01.372691Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:40:58.803457Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:42:07.863699Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T09:43:11.877596Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T09:44:20.926571Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T15:45:18.363420Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_193_MINER-10-102-0-193.txt
10.102.0.194 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:1,2,3 | 2026-05-03T06:12:11.340013Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:16.493531Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:21.646853Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:26.830690Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:31.983288Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:37.137380Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:42.290732Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:47.442256Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:52.626947Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:12:57.781859Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:13:02.935565Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:13:08.090697Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_194_MINER-10-102-0-194.txt
10.102.0.197 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-05-02T12:06:58.173493Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:03.315802Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:08.481117Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:13.622269Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:18.763758Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:23.929725Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:29.072409Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:34.215746Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:39.359192Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:44.503664Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:49.646687Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-02T12:07:54.791364Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_197_MINER-10-102-0-197.txt
10.102.0.199 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-28T20:50:49.857786Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:52:20.016112Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:53:44.858405Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:59:20.596698Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:00:49.953611Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:02:15.489350Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:04:55.016231Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:16:06.898946Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:17:40.806346Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:03:21.309438Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:04:56.271022Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:06:23.753755Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_199_MINER-10-102-0-199.txt
10.102.0.206 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-27T05:53:05.716178Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:23:35.992977Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:24:45.568565Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T09:19:47.878858Z [ERROR] Tuner error: {ERR:H2} Stage 9: Zero MCR on hashboards [Address(2)] 2026-04-27T09:27:53.258254Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-27T09:39:09.355748Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T09:40:21.862303Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T10:41:22.035678Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T10:42:31.595117Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T16:43:41.537438Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T16:45:08.972706Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T22:46:18.067072Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_206_MINER-10-102-0-206.txt
10.102.0.208 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-26T20:50:49.422581Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(1)] 2026-04-26T21:02:45.351130Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:12:49.019968Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(3)] 2026-04-26T21:35:11.832684Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:37:53.843025Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I1} unexpected revision of chip 3 (expected: 0x1366 received: 0xc30) 2026-04-26T21:46:41.075901Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(1)] 2026-04-26T21:57:21.176302Z [ERROR] Tuner error: {ERR:H2} Stage 13: Zero MCR on hashboards [Address(1)] 2026-04-26T22:09:17.428824Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:12:07.320714Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I1} unexpected revision of chip 3 (expected: 0x1366 received: 0x630) 2026-04-26T22:48:12.404990Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 199 chips, expected maximum 110 chips on one chain 2026-04-26T22:50:44.519111Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-26T22:52:17.593671Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_208_MINER-10-102-0-208.txt
10.102.0.210 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-25T15:20:14.670396Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T03:39:37.390801Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T03:48:45.034210Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-04-26T20:53:10.297842Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-26T21:13:48.379556Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I2} detected 468 chips, expected maximum 110 chips on one chain 2026-04-27T05:34:37.661275Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 1 (expected: 0x1366 received: 0x2) 2026-04-27T05:35:45.594962Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T16:42:35.528444Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-27T18:20:03.821960Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-27T19:52:44.252992Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-27T20:37:39.441451Z [ERROR] Tuner error: {ERR:H2} Stage 8: Zero MCR on hashboards [Address(1)] 2026-04-27T20:49:28.911208Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_210_MINER-10-102-0-210.txt
10.102.0.211 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-27T04:12:57.778511Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:42:42.194864Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:43:51.252720Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:44:59.524491Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:46:11.159208Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:53:53.921913Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:26:56.242568Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:27:59.491342Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1), Address(3)] 2026-04-28T03:54:06.803347Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] 2026-04-28T04:33:36.705168Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-28T04:34:40.756466Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(3)] 2026-04-28T06:53:54.311165Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(1)] | logs_10_102_0_211_MINER-10-102-0-211.txt
10.102.0.215 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-04-29T02:59:16.004584Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T03:10:13.984571Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T03:11:23.059395Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-29T03:44:55.839113Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T03:46:04.912107Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-29T03:47:13.177843Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T03:48:24.757807Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T03:59:23.129495Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T04:00:32.201363Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-29T05:01:37.833214Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-29T05:02:45.249582Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I1} unexpected revision of chip 28 (expected: 0x1366 received: 0x0) 2026-04-29T11:03:42.679255Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing | logs_10_102_0_215_MINER-10-102-0-215.txt
10.102.0.217 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1,2,3 | 2026-05-01T17:40:27.744456Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:40:32.884702Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:40:38.032809Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:40:43.173120Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:40:48.313401Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:40:53.453278Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:40:58.593653Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:41:03.739134Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:41:08.882852Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:41:14.026021Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:41:19.196449Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-01T17:41:24.335328Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_217_MINER-10-102-0-217.txt
10.102.0.221 | 无算力(0TH/s) | 0.000000 | 温度传感器通信失败（误报超温/温差保护停机） | 高 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | CONFIG 中 IsPowerSupplyOn 为 false：多为保护关机或未上电；请先查温度传感器排线/接口，再尝试唤醒或手动上电 | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-05-03T06:16:56.517324Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:16:58.114488Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:16:59.711690Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:17:01.313297Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:17:02.910267Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:17:04.371168Z [ERROR] connection dropped due to pool inactivity 2026-05-03T06:17:04.371407Z [ERROR] Stratum read failure 2026-05-03T06:17:04.372050Z [INFO] Connection closed by the server 2026-05-03T06:17:04.502942Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:17:06.100277Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:17:07.699753Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:17:09.298989Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_221_MINER-10-102-0-221.txt
10.102.0.223 | 无算力(0TH/s) | 0.000000 | 算力板 EEPROM 读取失败（多链初始化失败，SOC 无法启动） | 高 | 矿机服务异常/接口超时；多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 多链 EEPROM 无数据/校验/Fixture 失败会导致 SOC 无法完成基本初始化；优先排查排线与固件，再考虑控制板/算力板 | 根据 load chain … eeprom / Data load fail / eeprom load ret:-1 定位失败链；逐链重插数据排线与电源，换槽位交叉测试区分板卡与控制板；EEPROM error: CRC … REGION、Fixture data load failed 多为数据损坏或通信问题；多链同时失败优先查共因（排线、控制板 EEPROM 通路、固件版本）；出现 ERROR_SOC_INIT: basic init failed / stop_mining: basic init failed 时，勿先当总线泛化故障；可尝试重刷官方或兼容固件后再测；若单链异常可换板；多链皆失败且排除连接后重点考虑控制板或批量硬件问题 | [ 0.523180@0] clkmsr ffd18004.meson_clk_msr: failed to get msr ring reg0 [ 0.638304@0] dmi: Firmware registration failed. [ 1.510569@2] Initramfs unpacking failed: junk in compressed archive [ 2.007017@2] i2c i2c-1: of_i2c: modalias failure on /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 2.010797@2] i2c i2c-1: Failed to create I2C device for /soc/aobus@ff800000/i2c@5000/mcu6350@40 [ 3.168464@2] defendkey: probe of defendkey failed with error -22 [ 3.916668@2] hub 2-0:1.0: config failed, hub doesn't have any ports! (err -19) [ 4.082357@0] thermal thermal_zone0: binding zone soc_thermal with cdev thermal-cpufreq-0 failed:-22 [ 5.755531@0] meson6-dwmac ff3f0000.ethernet eth0: fail to init PTP. 2026-05-03 03:01:53 get test_loop_securely_find_asic_num failed 2026-05-03 03:02:00 fail to write 0:1 2026-05-03 03:02:00 fail to read 0:1 | logs_10_102_0_223_MINER-10-102-0-223.txt
10.102.1.62 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-28T20:49:04.958940Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:50:37.639838Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:52:14.271966Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:53:41.712140Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T20:59:05.833763Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:00:44.074190Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:02:13.161915Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:03:38.090724Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:14:49.126464Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T21:16:23.196131Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:03:06.100003Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:04:39.999790Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_62_MINER-10-102-1-62.txt
10.102.1.63 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-27T05:39:07.777553Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T06:40:07.360091Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T06:41:14.779538Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:23:02.493444Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:24:11.567509Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:25:19.836773Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:26:31.390949Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:37:29.534922Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:38:38.603649Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T09:39:42.601355Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T09:40:51.653321Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T15:41:49.073031Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_63_MINER-10-102-1-63.txt
10.102.1.64 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；总线/通信异常；网络/矿池连接异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-27T13:11:51.097199Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T13:13:11.623861Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T14:26:59.486811Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 9 (expected: 0x1366 received: 0x0) 2026-04-27T15:32:50.425251Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 16 (expected: 0x1366 received: 0x426) 2026-04-27T15:35:38.193534Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T05:06:20.919702Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T05:07:39.763818Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T05:09:40.857483Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-28T06:14:38.329149Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T06:26:04.172828Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 3 (expected: 0x1366 received: 0x8) 2026-04-28T06:27:30.462745Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T07:28:53.682694Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I2} detected 319 chips, expected maximum 110 chips on one chain | logs_10_102_1_64_MINER-10-102-1-64.txt
10.102.1.65 | 无算力(0TH/s) | 0.000000 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；总线/通信异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-28T22:10:38.787927Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:21:51.789350Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T22:24:39.549848Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-28T23:25:48.641736Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-28T23:27:18.666830Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-29T02:55:47.837990Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-29T02:57:21.227542Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-29T02:59:26.725421Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-29T03:01:34.190945Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-29T03:12:34.080299Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-29T03:14:07.516503Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-29T03:44:55.790896Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_65_MINER-10-102-1-65.txt
10.102.1.67 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-30T16:17:58.000401Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-30T17:19:05.342690Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-30T17:19:05.351840Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-04-30T17:20:15.074812Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-04-30T17:20:15.087663Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T00:16:34.991085Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T00:16:35.001286Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T00:17:52.071092Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T00:17:52.080424Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:42:49.424403Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:42:49.433752Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:44:05.488245Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_1_67_MINER-10-102-1-67.txt
10.102.1.72 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-05-01T01:55:55.146453Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:55:55.155580Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 6 (expected: 0x1366 received: 0xf00) 2026-05-01T01:58:51.314795Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:58:51.324188Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 14 of read_register(reg=0x0) doesn't match chip count 110: reply 0x8 missing 2026-05-01T02:00:06.874955Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:00:06.885572Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-05-01T02:01:19.267298Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:01:19.276740Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-05-01T02:02:32.183061Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:02:32.192168Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) 2026-05-01T02:13:35.262516Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T02:13:35.275362Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I1} unexpected revision of chip 2 (expected: 0x1366 received: 0x0) | logs_10_102_1_72_MINER-10-102-1-72.txt
10.102.1.73 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 算力板/芯片异常；网络/矿池连接异常；总线/通信异常；矿机服务异常/接口超时；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；总线/通信异常 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-27T04:23:17.102049Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:25:46.786397Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T04:26:56.372361Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:26:52.876398Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T08:28:04.493538Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T17:53:47.906170Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T17:55:15.906044Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T17:57:01.152437Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T17:59:14.124794Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-27T19:03:55.432228Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-27T19:05:30.365898Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-27T20:14:09.639870Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_73_MINER-10-102-1-73.txt
10.102.1.75 | 无算力(0TH/s) | 0.000000 | 算力板芯片枚举不足（Hashchip 与 110 不符，已被禁用） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信 | 多链芯片响应不足或无法通信，Tuner 已禁用对应算力板；优先重插排线/换槽位，仍失败则更换板卡；PSU I²C 校验失败可为次要因素，多在板卡与链路确认后再复测电源通信；算力板/芯片异常 | 根据 Tuner error / CHAIN 日志确认 {HB:n} 与「number of responses … doesn't match chip count 110」对应链；断电后重插故障板数据排线与电源接口；与正常链互换槽位判断是板卡还是槽位/控制板；仅一链正常时总算力约为额定三分之一属常见现象；PSU I²C checksum 异常多为次要，板卡稳定后再复测电源；若某链长期 0 响应或响应数远低于 110，按算力板硬件损坏或通信链路故障处理，更换板卡或送修；当前日志涉及 HB:1 | 2026-04-30T18:29:49.059456Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T00:30:51.961555Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T00:30:51.970821Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:28:05.299240Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:28:05.308347Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:42:10.585061Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:42:10.595242Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:43:26.679754Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:43:26.692512Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:45:53.289667Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons 2026-05-01T01:45:53.299174Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: Hashchip: number of responses 0 of read_register(reg=0x0) doesn't match chip count 110: reply 0x0 missing 2026-05-01T01:47:07.326997Z [ERROR] {ERR:H1} Hashboard 1 has a problem, but this is a NoPIC miner and bosminer can't disable it individually for safety reasons | logs_10_102_1_75_MINER-10-102-1-75.txt
10.102.1.77 | 无算力(0TH/s) | 0.000000 | 算力板严重异常（芯片识别/通信错误，NoPIC 可能无法单禁板） | 高 | 网络/矿池连接异常；算力板/芯片异常；矿机服务异常/接口超时；总线/通信异常；若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主 | 若混有较早的 Failed to resolve，通常与当前 tuner 禁板无直接关系，以 HB 报错为主；矿机服务异常/接口超时 | 关注 Tuner 报错：如 detected … chips 远超 110、unexpected revision、ERR:I1/I2，多为该板通信或硬件损坏；断电后重插故障 HB 对应算力板排线与供电；与正常板互换槽位判断是板还是接口；NoPIC 机型可能无法单独禁用故障板，整机可能无法继续挖矿，需先修复或更换该板；若混有历史 Failed to resolve，以导出时间附近 tuner/hashboard 报错为准；矿池 Alive 不等于当前无板级故障；当前日志涉及 HB:1,2,3 | 2026-04-17T01:57:41.425168Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:58:50.985511Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:41:29.180560Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:42:40.918876Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:54:45.228351Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:54.797216Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T12:38:30.128125Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-19T14:26:40.489845Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-19T14:51:58.049052Z [ERROR] Tuner error: {ERR:H2} Stage 1: Zero MCR on hashboards [Address(2)] 2026-04-19T17:38:47.253381Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:39:56.836740Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-20T16:58:28.887090Z [ERROR] Tuner error: miner resume: waiting for start: InitError on hashchain 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_1_77_MINER-10-102-1-77.txt

## 低算力
ip | status | ths_15m | primary_cause | confidence | alternate_causes | secondary_causes | solutions | evidence | file
10.102.0.162 | 低算力(<50TH/s) | 47.771210 | 温度传感器通信失败（误报超温/温差保护停机） | 高 |  |  | 根据日志确认 fail to read tsensor / pic temp 的 chain 号，检查该链算力板排线、PIC 传感器侧连接是否松动或氧化；与正常链交叉换槽位：故障随板走则更换算力板；固定在槽位则查控制板接口与线缆；若日志中 PCB/芯片温度读数明显低于上限仍报 ERROR_TEMP，多为传感器数据异常而非真实过热；确认对应链供电稳定；固件层面勿轻易关闭温度保护，优先硬件修复或更换故障板 | 2026-05-03T06:15:33.775808Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:35.371281Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:36.968744Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:38.568432Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:40.161526Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:41.759173Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:43.358797Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:44.956372Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:46.551508Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:48.149177Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:49.748898Z [WARN] Temperature Sensor Read Failed 2026-05-03T06:15:51.344112Z [WARN] Temperature Sensor Read Failed | logs_10_102_0_162_MINER-10-102-0-162.txt
10.102.0.174 | 低算力(<50TH/s) | 36.177077 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,2,3 | 2026-04-16T19:30:23.989661Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T22:57:33.626113Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T22:58:58.830976Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:54:48.639817Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:56:09.860848Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:57:41.699354Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:58:49.638738Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:41:24.237540Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-17T05:42:33.820194Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:54:12.974860Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:24.401498Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-19T17:39:37.311693Z [ERROR] Tuner error: Disabled hashboard 2 {HB:2}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_174_MINER-10-102-0-174.txt
10.102.0.213 | 低算力(<50TH/s) | 41.460135 | 算力板全板失效（芯片未检出/初始化失败） | 高 | 算力板/芯片异常；网络/矿池连接异常；矿机服务异常/接口超时；疑似供电/排线/控制板链路问题 | 疑似供电/排线/控制板链路问题；算力板/芯片异常 | 断电后重新插拔控制板到三块算力板的数据排线与电源接口；重点检查 HB1/HB2/HB3 是否都出现 no chips detected 或 NoChipsDetected；交叉测试控制板与算力板，确认是控制板链路问题还是算力板损坏；检查 PSU 对算力板供电电压与负载稳定性（是否触发过流保护）；若仍失败，优先更换故障算力板或控制板；当前日志涉及 HB:1,3 | 2026-04-15T23:42:54.112824Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-15T23:44:36.223520Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T14:12:32.171279Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-16T14:13:45.428336Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T19:29:13.137255Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-16T19:30:38.371121Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:55:07.436139Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-16T23:56:34.691817Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:57:18.820070Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-17T01:58:28.392112Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:54:08.697631Z [ERROR] Tuner error: Disabled hashboard 1 {HB:1}: {ERR:I3} no chips detected on the current chain 2026-04-18T09:55:18.271886Z [ERROR] Tuner error: Disabled hashboard 3 {HB:3}: {ERR:I3} no chips detected on the current chain | logs_10_102_0_213_MINER-10-102-0-213.txt
10.102.0.216 | 低算力(<50TH/s) | 30.372106 | 算力板 EEPROM 解析失败（ERR:E4，无法启动挖矿） | 高 | 算力板/芯片异常；矿机服务异常/接口超时；多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板 | 多为指定算力板 EEPROM 数据损坏或硬件故障；优先重插该板排线/换槽位，仍失败则更换算力板；算力板/芯片异常 | 根据日志定位无法解码的算力板编号（如 hashboard #2）；断电后重插该板数据排线与电源线，换槽位交叉测试判断是否随板损坏；EEPROM 数据异常（如全 0）多为板载存储或硬件故障，重复失败需更换算力板或送修；若同时出现 Failed to set up PSU / dummy backend，先在板卡与排线确认后再单独测 PSU 协议与供电稳定性；paused by dead pools / missing license 多为未成功启动挖矿的连带现象，优先解决 ERR:E4 与硬件后再看矿池与授权；当前日志涉及 HB:2,3 | 2026-05-03T06:01:07.431145Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:12.587302Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:17.739081Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:22.891793Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:28.044160Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:33.197445Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:38.350929Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:43.506386Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:48.661004Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:53.813861Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:01:58.968670Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) 2026-05-03T06:02:04.124018Z [ERROR] {ERR:E3} Reading hashboard EEPROM at address 2: No such device or address (os error 6) | logs_10_102_0_216_MINER-10-102-0-216.txt